## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 1 | 125 | 113 | 33 | 37.1 | 33.17 | 50 | 83.4 | 31.4 | 58.5 | 50.9 | 211.7 | 198.3 | 198.3 | NO
| NG | 125 | 12 | 113 | 33 | 37.1 | 30.42 | 50 | 83.4 | 31.4 | 60.5 | 48.5 | 211.3 | 206.1 | 206.1 | NO
| NG | 12 | 13 | 113 | 33 | 37.1 | 22.22 | 50 | 83.4 | 31.4 | 66.6 | 48.5 | 211 | 206.1 | 206.1 | NO
| NG | 13 | 14 | 113 | 33 | 37.1 | 22.22 | 50 | 83.4 | 31.4 | 66.6 | 46.8 | 211 | 205.8 | 205.8 | NO
| NG | 14 | 15 | 113 | 33 | 37.1 | 20.15 | 50 | 83.4 | 31.4 | 68.1 | 46.8 | 211 | 205.8 | 205.8 | NO
| NG | 15 | 10 | 113 | 33 | 37.1 | 19.24 | 50 | 83.4 | 31.4 | 68.7 | 46 | 211 | 207.6 | 207.6 | NO
| NG | 10 | 11 | 113 | 33 | 37.1 | 19.24 | 50 | 83.4 | 31.4 | 68.7 | 46 | 211 | 207.6 | 207.6 | NO
| NG | 11 | 93 | 113 | 33 | 37.1 | 18.45 | 50 | 83.4 | 31.4 | 69.3 | 45.4 | 211 | 208.8 | 208.8 | NO
| NG | 93 | 2 | 113 | 33 | 37.1 | 18.45 | 50 | 83.4 | 31.4 | 69.3 | 45.2 | 211 | 209.2 | 209.2 | NO
1 | OK | 2 | 7 | 123 | 33 | 107 | 5.52 | 50 | 83.4 | 31.4 | 79.1 | 32.9 | 210.6 | 213.3 | 210.6 | YES
2 | ** OPTIMAL ** | 2 | 109 | 113 | 33 | 37.1 | 12.38 | 50 | 83.4 | 31.4 | 73.7 | 40.6 | 210.8 | 212.7 | 210.8 | YES
3 | OK | 109 | 128 | 113 | 33 | 37.1 | 12.15 | 50 | 83.4 | 31.4 | 73.9 | 40.6 | 210.7 | 212.7 | 210.7 | YES
4 | OK | 128 | 114 | 113 | 33 | 37.1 | 12.15 | 50 | 83.4 | 31.4 | 73.9 | 40.2 | 210.7 | 212.7 | 210.7 | YES
5 | OK | 114 | 110 | 113 | 33 | 37.1 | 11.63 | 50 | 83.4 | 31.4 | 74.3 | 40.2 | 210.7 | 212.7 | 210.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-014092
TR_B (available) | 58-016607
TR_A Rated kVA | 160
TR_B Rated kVA | 160
TR_A Baseline Loading% | 83.4
TR_B Baseline Loading% | 31.4
Total Scenarios Evaluated | 14
Feasible Scenarios | 5
--- Optimal Solution ---
Switch Parent Node | 2
Switch Child Node | 109
Tie Node (TR_A side) | 113
Tie Node (TR_B side) | 33
Tie Line Distance (m) | 37.1
Load Transferred (kW) | 12.38
TR_A Loading After (%) | 73.7
TR_B Loading After (%) | 40.6
Minimum Voltage (V) | 210.8