## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 117 | 115 | 108 | 24 | 65.5 | 49.7 | 50 | 99.2 | 11.9 | 39.3 | 31.4 | 221.7 | 162.2 | 162.2 | NO
| NG | 115 | 51 | 108 | 24 | 65.5 | 49.7 | 50 | 99.2 | 11.9 | 39.3 | 31.4 | 221.7 | 162.2 | 162.2 | NO
| NG | 51 | 52 | 108 | 24 | 65.5 | 38.99 | 50 | 99.2 | 11.9 | 51.6 | 26.7 | 220.9 | 178.2 | 178.2 | NO
1 | ** OPTIMAL ** | 52 | 17 | 6 | 22 | 67.9 | 24.57 | 50 | 99.2 | 11.9 | 61.6 | 20.2 | 219.7 | 211.2 | 211.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-016375
TR_B (available) | 59-011610
TR_A Rated kVA | 100
TR_B Rated kVA | 160
TR_A Baseline Loading% | 99.2
TR_B Baseline Loading% | 11.9
Total Scenarios Evaluated | 4
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 52
Switch Child Node | 17
Tie Node (TR_A side) | 6
Tie Node (TR_B side) | 22
Tie Line Distance (m) | 67.9
Load Transferred (kW) | 24.57
TR_A Loading After (%) | 61.6
TR_B Loading After (%) | 20.2
Minimum Voltage (V) | 211.2