## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 30 | 12 | 51 | 5 | 146.3 | 13.62 | 50 | 87 | 11.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 30 | 31 | 43 | 7 | 8.6 | 8.27 | 50 | 87 | 11.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 12 | 13 | 51 | 5 | 146.3 | 2.38 | 50 | 87 | 11.7 | 77.6 | 21.1 | 196.7 | 220.6 | 196.7 | NO
| NG | 12 | 24 | 14 | 7 | 149.1 | 11.24 | 50 | 87 | 11.7 | 41 | 59.1 | 219.7 | 193.5 | 193.5 | NO
| NG | 31 | 64 | 43 | 7 | 8.6 | 6.66 | 50 | 87 | 11.7 | 61.1 | 37.9 | 200 | 216.5 | 200 | NO
| NG | 13 | 44 | 51 | 5 | 146.3 | 2.14 | 50 | 87 | 11.7 | 78.5 | 20.1 | 196.4 | 221.5 | 196.4 | NO
| NG | 24 | 1 | 14 | 7 | 149.1 | 9.97 | 50 | 87 | 11.7 | 45.8 | 53 | 218.8 | 199.3 | 199.3 | NO
| NG | 64 | 33 | 43 | 7 | 8.6 | 6.58 | 50 | 87 | 11.7 | 61.4 | 37.6 | 200 | 216.6 | 200 | NO
| NG | 1 | 0 | 14 | 7 | 149.1 | 9.97 | 50 | 87 | 11.7 | 45.8 | 53 | 218.8 | 199.3 | 199.3 | NO
| NG | 33 | 32 | 43 | 7 | 8.6 | 6.45 | 50 | 87 | 11.7 | 61.9 | 37.1 | 199.9 | 216.9 | 199.9 | NO
| NG | 0 | 9 | 14 | 7 | 149.1 | 9.49 | 50 | 87 | 11.7 | 47.7 | 50.7 | 218.4 | 201.3 | 201.3 | NO
| NG | 32 | 34 | 43 | 7 | 8.6 | 5.79 | 50 | 87 | 11.7 | 64.4 | 34.4 | 199.3 | 218 | 199.3 | NO
| NG | 9 | 8 | 14 | 7 | 149.1 | 9.42 | 50 | 87 | 11.7 | 48 | 50.4 | 218.4 | 201.6 | 201.6 | NO
| NG | 34 | 45 | 43 | 7 | 8.6 | 5.28 | 50 | 87 | 11.7 | 66.4 | 32.3 | 198.9 | 218.9 | 198.9 | NO
1 | OK | 8 | 4 | 14 | 7 | 149.1 | 6.93 | 50 | 87 | 11.7 | 57.7 | 39.3 | 215.7 | 212.3 | 212.3 | YES
| NG | 45 | 46 | 10 | 4 | 54.2 | 2.58 | 50 | 87 | 11.7 | 76.8 | 21.7 | 196.4 | 223.2 | 196.4 | NO
| NG | 45 | 58 | 43 | 7 | 8.6 | 2.7 | 50 | 87 | 11.7 | 76.4 | 22.1 | 196.6 | 224.2 | 196.6 | NO
2 | OK | 4 | 5 | 14 | 7 | 149.1 | 6.75 | 50 | 87 | 11.7 | 58.4 | 38.6 | 215.4 | 212.9 | 212.9 | YES
| NG | 46 | 38 | 10 | 4 | 54.2 | 2.15 | 50 | 87 | 11.7 | 78.5 | 20 | 196.1 | 223.9 | 196.1 | NO
| NG | 58 | 59 | 43 | 7 | 8.6 | 2.55 | 50 | 87 | 11.7 | 77 | 21.5 | 196.4 | 224.4 | 196.4 | NO
3 | ** OPTIMAL ** | 5 | 16 | 14 | 7 | 149.1 | 6.27 | 50 | 87 | 11.7 | 60.3 | 36.6 | 214.5 | 214.4 | 214.4 | YES
4 | OK | 16 | 17 | 14 | 7 | 149.1 | 6.03 | 50 | 87 | 11.7 | 61.2 | 35.6 | 214.1 | 215.1 | 214.1 | YES
5 | OK | 17 | 6 | 14 | 7 | 149.1 | 5.78 | 50 | 87 | 11.7 | 62.2 | 34.5 | 213.6 | 215.8 | 213.6 | YES
6 | OK | 6 | 20 | 14 | 7 | 149.1 | 4.61 | 50 | 87 | 11.7 | 67 | 29.8 | 210.8 | 219.3 | 210.8 | YES
| NG | 20 | 21 | 14 | 7 | 149.1 | 3.78 | 50 | 87 | 11.7 | 70.4 | 26.4 | 208.6 | 221.4 | 208.6 | NO
| NG | 21 | 49 | 14 | 7 | 149.1 | 3.39 | 50 | 87 | 11.7 | 72 | 24.9 | 207.5 | 222.1 | 207.5 | NO
| NG | 49 | 48 | 14 | 7 | 149.1 | 3.13 | 50 | 87 | 11.7 | 73.1 | 23.9 | 206.7 | 222.5 | 206.7 | NO
| NG | 48 | 15 | 14 | 7 | 149.1 | 2.11 | 50 | 87 | 11.7 | 77.5 | 19.9 | 202.6 | 224.6 | 202.6 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 60-021805
TR_B (available) | 66-014071
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 87
TR_B Baseline Loading% | 11.7
Total Scenarios Evaluated | 28
Feasible Scenarios | 6
--- Optimal Solution ---
Switch Parent Node | 5
Switch Child Node | 16
Tie Node (TR_A side) | 14
Tie Node (TR_B side) | 7
Tie Line Distance (m) | 149.1
Load Transferred (kW) | 6.27
TR_A Loading After (%) | 60.3
TR_B Loading After (%) | 36.6
Minimum Voltage (V) | 214.4