## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 11 | 12 | 19 | 10 | 22.6 | 5.98 | 50 | 82.6 | 8.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 11 | 10 | 10 | 11 | 131.1 | 15.42 | 50 | 82.6 | 8.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 12 | 67 | 67 | 11 | 107.3 | 1.65 | 50 | 82.6 | 8.5 | 76.3 | 14.1 | 216.6 | 225.2 | 216.6 | YES
2 | OK | 12 | 68 | 19 | 10 | 22.6 | 4.33 | 50 | 82.6 | 8.5 | 66 | 16.5 | 217.1 | 222.4 | 217.1 | YES
| NG | 10 | 5 | 5 | 11 | 165.3 | 14.34 | 50 | 82.6 | 8.5 | 27 | 35.1 | 225.5 | 203.6 | 203.6 | NO
3 | OK | 67 | 14 | 14 | 11 | 116.3 | 1.39 | 50 | 82.6 | 8.5 | 77.3 | 13.1 | 216.4 | 226 | 216.4 | YES
4 | OK | 68 | 19 | 19 | 10 | 22.6 | 4 | 50 | 82.6 | 8.5 | 67.2 | 16.5 | 217.1 | 222.4 | 217.1 | YES
| NG | 5 | 4 | 4 | 11 | 196 | 13.66 | 50 | 82.6 | 8.5 | 29.6 | 35.1 | 225.5 | 203.6 | 203.6 | NO
5 | OK | 19 | 20 | 20 | 10 | 24.8 | 2.05 | 50 | 82.6 | 8.5 | 67.2 | 16.5 | 217.1 | 222.4 | 217.1 | YES
| NG | 4 | 7 | 7 | 11 | 205.7 | 12.89 | 50 | 82.6 | 8.5 | 32.6 | 35.1 | 225.5 | 203.6 | 203.6 | NO
6 | OK | 20 | 39 | 39 | 10 | 222.5 | 2.05 | 50 | 82.6 | 8.5 | 74.7 | 16.5 | 217.1 | 221.7 | 217.1 | YES
7 | ** OPTIMAL ** | 7 | 6 | 6 | 11 | 210.3 | 2.74 | 50 | 82.6 | 8.5 | 71.9 | 17.5 | 218.2 | 220 | 218.2 | YES
8 | OK | 7 | 28 | 28 | 11 | 212.8 | 5.5 | 50 | 82.6 | 8.5 | 61.2 | 14.1 | 217.1 | 224.8 | 217.1 | YES
9 | OK | 7 | 36 | 36 | 11 | 214.2 | 4.65 | 50 | 82.6 | 8.5 | 64.4 | 19.1 | 220.7 | 216.6 | 216.6 | YES
10 | OK | 6 | 8 | 8 | 11 | 222.4 | 1.99 | 50 | 82.6 | 8.5 | 74.8 | 14.5 | 217.3 | 222.5 | 217.3 | YES
11 | OK | 28 | 29 | 29 | 11 | 230.3 | 3.13 | 50 | 82.6 | 8.5 | 70.4 | 20.8 | 215.4 | 218.9 | 215.4 | YES
12 | OK | 28 | 30 | 30 | 11 | 214.6 | 2.37 | 50 | 82.6 | 8.5 | 73.4 | 14.1 | 217.2 | 224.9 | 217.2 | YES
13 | OK | 36 | 3 | 3 | 11 | 239.3 | 4.64 | 50 | 82.6 | 8.5 | 64.4 | 19.1 | 220.7 | 216.6 | 216.6 | YES
14 | OK | 8 | 9 | 44 | 10 | 229 | 1.68 | 50 | 82.6 | 8.5 | 76 | 14.6 | 217.4 | 220.7 | 217.4 | YES
15 | OK | 29 | 31 | 31 | 11 | 261.6 | 2.9 | 50 | 82.6 | 8.5 | 71.2 | 19.9 | 215.4 | 219.7 | 215.4 | YES
16 | OK | 30 | 27 | 26 | 9 | 215 | 1.95 | 50 | 82.6 | 8.5 | 75 | 12.5 | 216.7 | 225.9 | 216.7 | YES
17 | OK | 3 | 2 | 2 | 11 | 273.6 | 3.58 | 50 | 82.6 | 8.5 | 68.6 | 19.1 | 220 | 216.6 | 216.6 | YES
18 | OK | 9 | 25 | 44 | 10 | 229 | 1.56 | 50 | 82.6 | 8.5 | 76.5 | 14.6 | 217.4 | 220.7 | 217.4 | YES
19 | OK | 2 | 1 | 38 | 11 | 282.2 | 2.67 | 50 | 82.6 | 8.5 | 72.1 | 19.1 | 218.9 | 216.4 | 216.4 | YES
20 | OK | 25 | 42 | 42 | 11 | 248.2 | 1.03 | 50 | 82.6 | 8.5 | 78.6 | 12.5 | 216.7 | 224.3 | 216.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-021903
TR_B (available) | 47-000525
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 82.6
TR_B Baseline Loading% | 8.5
Total Scenarios Evaluated | 25
Feasible Scenarios | 20
--- Optimal Solution ---
Switch Parent Node | 7
Switch Child Node | 6
Tie Node (TR_A side) | 6
Tie Node (TR_B side) | 11
Tie Line Distance (m) | 210.3
Load Transferred (kW) | 2.74
TR_A Loading After (%) | 71.9
TR_B Loading After (%) | 17.5
Minimum Voltage (V) | 218.2