## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 34 | 33 | 14 | 33 | 14 | 29.81 | 95 | 78.9 | 41.8 | 44.4 | 63.6 | 215.5 | 219 | 215.5 | YES
| NG | 34 | 55 | 46 | 29 | 73.7 | 37.56 | 50 | 78.9 | 41.8 | 34.5 | 75.7 | 224.4 | 167 | 167 | NO
2 | OK | 33 | 76 | 14 | 33 | 14 | 29.81 | 95 | 78.9 | 41.8 | 44.4 | 63.6 | 215.5 | 219 | 215.5 | YES
| NG | 55 | 50 | 46 | 29 | 73.7 | 37.56 | 50 | 78.9 | 41.8 | 34.5 | 75.7 | 224.4 | 167 | 167 | NO
3 | OK | 76 | 75 | 14 | 33 | 14 | 27.67 | 95 | 78.9 | 41.8 | 46.8 | 62.1 | 215.5 | 219 | 215.5 | YES
4 | OK | 76 | 78 | 78 | 65 | 63.3 | 2.14 | 50 | 78.9 | 41.8 | 76.5 | 43.4 | 213.3 | 220.5 | 213.3 | YES
| NG | 50 | 51 | 46 | 29 | 73.7 | 37.56 | 50 | 78.9 | 41.8 | 34.5 | 75.7 | 224.4 | 167 | 167 | NO
5 | OK | 75 | 74 | 14 | 33 | 14 | 27.67 | 95 | 78.9 | 41.8 | 46.8 | 62.1 | 215.5 | 219 | 215.5 | YES
| NG | 51 | 77 | 46 | 29 | 73.7 | 37.54 | 50 | 78.9 | 41.8 | 34.5 | 75.6 | 224.4 | 167 | 167 | NO
6 | OK | 74 | 54 | 14 | 33 | 14 | 27.67 | 95 | 78.9 | 41.8 | 46.8 | 61.5 | 215.5 | 219.1 | 215.5 | YES
| NG | 77 | 7 | 46 | 29 | 73.7 | 37.54 | 50 | 78.9 | 41.8 | 34.5 | 75.6 | 224.4 | 167 | 167 | NO
7 | OK | 54 | 80 | 14 | 33 | 14 | 1.15 | 95 | 78.9 | 41.8 | 77.6 | 42.7 | 213.4 | 220.6 | 213.4 | YES
| NG | 54 | 72 | 1 | 64 | 34.7 | 25.78 | 50 | 78.9 | 41.8 | 49 | 49.3 | 215.5 | 204.3 | 204.3 | NO
| NG | 7 | 8 | 46 | 29 | 73.7 | 37.33 | 50 | 78.9 | 41.8 | 34.8 | 75.4 | 224.4 | 166.8 | 166.8 | NO
| NG | 72 | 73 | 1 | 64 | 34.7 | 25.78 | 50 | 78.9 | 41.8 | 49 | 49.3 | 215.5 | 204.3 | 204.3 | NO
| NG | 8 | 25 | 46 | 29 | 73.7 | 37.15 | 50 | 78.9 | 41.8 | 35 | 75.2 | 224.3 | 166.6 | 166.6 | NO
| NG | 73 | 52 | 1 | 64 | 34.7 | 22.57 | 50 | 78.9 | 41.8 | 52.7 | 47.9 | 215.1 | 208.4 | 208.4 | NO
| NG | 25 | 16 | 46 | 29 | 73.7 | 36.62 | 50 | 78.9 | 41.8 | 35.6 | 74.7 | 224.2 | 166.2 | 166.2 | NO
| NG | 52 | 5 | 1 | 64 | 34.7 | 20.1 | 50 | 78.9 | 41.8 | 55.5 | 47.9 | 215.1 | 208.4 | 208.4 | NO
| NG | 16 | 17 | 46 | 29 | 73.7 | 29.49 | 50 | 78.9 | 41.8 | 43.8 | 66.8 | 223.7 | 191.8 | 191.8 | NO
8 | OK | 16 | 29 | 9 | 3 | 87.8 | 7.13 | 50 | 78.9 | 41.8 | 70.5 | 47.2 | 216.1 | 220.1 | 216.1 | YES
9 | OK | 5 | 6 | 1 | 64 | 34.7 | 17.5 | 50 | 78.9 | 41.8 | 58.5 | 46.6 | 214.8 | 211.7 | 211.7 | YES
10 | OK | 5 | 24 | 3 | 62 | 55 | 2.6 | 50 | 78.9 | 41.8 | 75.9 | 43.4 | 213.7 | 220.7 | 213.7 | YES
| NG | 17 | 10 | 46 | 29 | 73.7 | 28.49 | 50 | 78.9 | 41.8 | 44.3 | 3.3468e+59 | 223.6 | 2792004.3 | 223.6 | NO
11 | OK | 29 | 28 | 9 | 3 | 87.8 | 3.72 | 50 | 78.9 | 41.8 | 74.5 | 44.6 | 214.9 | 220.7 | 214.9 | YES
12 | OK | 6 | 18 | 1 | 64 | 34.7 | 14.05 | 50 | 78.9 | 41.8 | 62.5 | 44.9 | 214.3 | 216.2 | 214.3 | YES
13 | OK | 24 | 4 | 3 | 62 | 55 | 1.05 | 50 | 78.9 | 41.8 | 77.7 | 42.3 | 213.4 | 220.6 | 213.4 | YES
| NG | 10 | 11 | 46 | 29 | 73.7 | 28.48 | 50 | 78.9 | 41.8 | 44.9 | 65.8 | 223.4 | 193.9 | 193.9 | NO
14 | OK | 28 | 27 | 9 | 3 | 87.8 | 3.72 | 50 | 78.9 | 41.8 | 74.5 | 43.6 | 214.9 | 220.5 | 214.9 | YES
15 | OK | 18 | 19 | 1 | 64 | 34.7 | 12.92 | 50 | 78.9 | 41.8 | 63.8 | 44.5 | 214.2 | 217.1 | 214.2 | YES
| NG | 11 | 30 | 46 | 29 | 73.7 | 27.38 | 50 | 78.9 | 41.8 | 46.2 | 64.7 | 223.4 | 196.1 | 196.1 | NO
16 | OK | 27 | 26 | 9 | 3 | 87.8 | 0.31 | 50 | 78.9 | 41.8 | 78.6 | 42.1 | 213.4 | 220.4 | 213.4 | YES
17 | OK | 19 | 20 | 1 | 64 | 34.7 | 11.19 | 50 | 78.9 | 41.8 | 65.8 | 44.5 | 214.2 | 217.1 | 214.2 | YES
| NG | 30 | 12 | 46 | 29 | 73.7 | 27.38 | 50 | 78.9 | 41.8 | 46.2 | 64.7 | 223.4 | 196.1 | 196.1 | NO
18 | OK | 26 | 9 | 9 | 3 | 87.8 | 0.1 | 50 | 78.9 | 41.8 | 78.8 | 41.9 | 213.4 | 220.5 | 213.4 | YES
19 | OK | 20 | 21 | 1 | 64 | 34.7 | 8.5 | 50 | 78.9 | 41.8 | 68.9 | 43.4 | 213.8 | 219.5 | 213.8 | YES
| NG | 12 | 13 | 46 | 29 | 73.7 | 26.15 | 50 | 78.9 | 41.8 | 47.6 | 63.6 | 223.4 | 195.6 | 195.6 | NO
20 | OK | 21 | 22 | 1 | 64 | 34.7 | 4.98 | 50 | 78.9 | 41.8 | 73 | 43.4 | 213.9 | 219.5 | 213.9 | YES
| NG | 13 | 31 | 46 | 29 | 73.7 | 25.25 | 50 | 78.9 | 41.8 | 47.6 | 62.8 | 223.4 | 195.3 | 195.3 | NO
21 | OK | 22 | 1 | 1 | 64 | 34.7 | 2.09 | 50 | 78.9 | 41.8 | 76.5 | 43.4 | 213.9 | 219.5 | 213.9 | YES
| NG | 31 | 32 | 46 | 29 | 73.7 | 22.41 | 50 | 78.9 | 41.8 | 52 | 60.1 | 223.1 | 201.6 | 201.6 | NO
22 | OK | 1 | 2 | 2 | 64 | 64.5 | 2.09 | 50 | 78.9 | 41.8 | 76.5 | 43.4 | 213.9 | 219.5 | 213.9 | YES
| NG | 32 | 35 | 46 | 29 | 73.7 | 21.49 | 50 | 78.9 | 41.8 | 53 | 59 | 223 | 203 | 203 | NO
23 | OK | 2 | 23 | 23 | 64 | 66.6 | 0.64 | 50 | 78.9 | 41.8 | 78.2 | 42.3 | 213.5 | 220.6 | 213.5 | YES
| NG | 35 | 44 | 46 | 29 | 73.7 | 18.5 | 50 | 78.9 | 41.8 | 56.5 | 56.7 | 222.2 | 203.7 | 203.7 | NO
24 | OK | 35 | 37 | 36 | 64 | 128.6 | 1.52 | 50 | 78.9 | 41.8 | 77.1 | 42.1 | 213.6 | 220.6 | 213.6 | YES
| NG | 44 | 41 | 46 | 29 | 73.7 | 18.5 | 50 | 78.9 | 41.8 | 56.5 | 56.7 | 222.2 | 203.7 | 203.7 | NO
| NG | 37 | 36 | 36 | 64 | 128.6 | 1.25 | 50 | 78.9 | 41.8 | [5 empty] | NO | TR_A sim: loading 2066% (degenerate)
25 | OK | 41 | 43 | 46 | 29 | 73.7 | 10.06 | 50 | 78.9 | 41.8 | 66.6 | 49.7 | 219.6 | 214.5 | 214.5 | YES
26 | OK | 43 | 60 | 46 | 29 | 73.7 | 7.77 | 50 | 78.9 | 41.8 | 69.4 | 47.8 | 217.8 | 215.7 | 215.7 | YES
27 | ** OPTIMAL ** | 60 | 61 | 46 | 29 | 73.7 | 7.09 | 50 | 78.9 | 41.8 | 70.2 | 47.3 | 217.8 | 217.4 | 217.4 | YES
28 | OK | 61 | 62 | 46 | 29 | 73.7 | 5.66 | 50 | 78.9 | 41.8 | 71.9 | 46.2 | 216.7 | 218.2 | 216.7 | YES
29 | OK | 62 | 63 | 46 | 29 | 73.7 | 4.36 | 50 | 78.9 | 41.8 | 73.5 | 45.2 | 216.8 | 217.6 | 216.8 | YES
30 | OK | 63 | 46 | 46 | 29 | 73.7 | 2.53 | 50 | 78.9 | 41.8 | 75.8 | 43.8 | 214.8 | 219.4 | 214.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-025728
TR_B (available) | 37-018453
TR_A Rated kVA | 100
TR_B Rated kVA | 160
TR_A Baseline Loading% | 78.9
TR_B Baseline Loading% | 41.8
Total Scenarios Evaluated | 54
Feasible Scenarios | 30
--- Optimal Solution ---
Switch Parent Node | 60
Switch Child Node | 61
Tie Node (TR_A side) | 46
Tie Node (TR_B side) | 29
Tie Line Distance (m) | 73.7
Load Transferred (kW) | 7.09
TR_A Loading After (%) | 70.2
TR_B Loading After (%) | 47.3
Minimum Voltage (V) | 217.4