## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 34 | 33 | 33 | 13 | 46.7 | 29.81 | 95 | 78.9 | 10.9 | 44.4 | 32.9 | 215.5 | 219.1 | 215.5 | YES
2 | OK | 34 | 55 | 77 | 13 | 3.3 | 37.56 | 95 | 78.9 | 10.9 | 34.5 | 39.1 | 224.4 | 210.7 | 210.7 | YES
3 | OK | 33 | 76 | 79 | 13 | 49.2 | 29.81 | 50 | 78.9 | 10.9 | 44.4 | 26.1 | 215.5 | 214.6 | 214.6 | YES
4 | OK | 55 | 50 | 77 | 13 | 3.3 | 37.56 | 95 | 78.9 | 10.9 | 34.5 | 39.1 | 224.4 | 210.7 | 210.7 | YES
5 | OK | 76 | 75 | 75 | 13 | 67.5 | 27.67 | 95 | 78.9 | 10.9 | 46.8 | 31.3 | 215.5 | 219.7 | 215.5 | YES
6 | OK | 76 | 78 | 79 | 13 | 49.2 | 2.14 | 50 | 78.9 | 10.9 | 76.5 | 12.4 | 213.3 | 227.4 | 213.3 | YES
7 | OK | 50 | 51 | 77 | 13 | 3.3 | 37.56 | 95 | 78.9 | 10.9 | 34.5 | 39.1 | 224.4 | 210.7 | 210.7 | YES
8 | OK | 75 | 74 | 74 | 13 | 76.4 | 27.67 | 95 | 78.9 | 10.9 | 46.8 | 31.3 | 215.5 | 219.7 | 215.5 | YES
9 | OK | 51 | 77 | 77 | 13 | 3.3 | 37.54 | 95 | 78.9 | 10.9 | 34.5 | 39.1 | 224.4 | 210.7 | 210.7 | YES
10 | OK | 74 | 54 | 72 | 13 | 78.1 | 27.67 | 50 | 78.9 | 10.9 | 46.8 | 30.8 | 215.5 | 219 | 215.5 | YES
11 | OK | 77 | 7 | 7 | 13 | 17.5 | 37.54 | 95 | 78.9 | 10.9 | 34.5 | 39.1 | 224.4 | 210.8 | 210.8 | YES
12 | OK | 54 | 80 | 80 | 13 | 92.4 | 1.15 | 95 | 78.9 | 10.9 | 77.6 | 11.7 | 213.4 | 227.3 | 213.4 | YES
13 | OK | 54 | 72 | 72 | 13 | 78.1 | 25.78 | 50 | 78.9 | 10.9 | 49 | 29.9 | 215.5 | 219.2 | 215.5 | YES
| NG | 7 | 8 | 81 | 23 | 33.9 | 37.33 | 50 | 78.9 | 10.9 | 34.8 | 23 | 224.4 | 198.8 | 198.8 | NO
14 | OK | 72 | 73 | 73 | 13 | 78.6 | 25.78 | 50 | 78.9 | 10.9 | 49 | 29.9 | 215.5 | 219.3 | 215.5 | YES
| NG | 8 | 25 | 81 | 23 | 33.9 | 37.15 | 50 | 78.9 | 10.9 | 35 | 23 | 224.3 | 198.8 | 198.8 | NO
15 | OK | 73 | 52 | 3 | 13 | 92.3 | 22.57 | 50 | 78.9 | 10.9 | 52.7 | 27.4 | 215.1 | 221.8 | 215.1 | YES
| NG | 25 | 16 | 81 | 23 | 33.9 | 36.62 | 50 | 78.9 | 10.9 | 35.6 | 23 | 224.2 | 198.8 | 198.8 | NO
16 | OK | 52 | 5 | 3 | 13 | 92.3 | 20.1 | 50 | 78.9 | 10.9 | 55.5 | 25.6 | 215.1 | 221.4 | 215.1 | YES
| NG | 16 | 17 | 81 | 23 | 33.9 | 29.49 | 50 | 78.9 | 10.9 | 43.8 | 19.4 | 223.7 | 208.1 | 208.1 | NO
17 | OK | 16 | 29 | 29 | 13 | 99.2 | 7.13 | 95 | 78.9 | 10.9 | 70.5 | 16 | 216.1 | 226.2 | 216.1 | YES
18 | OK | 5 | 6 | 6 | 13 | 116.8 | 17.5 | 50 | 78.9 | 10.9 | 58.5 | 23.6 | 214.8 | 223.1 | 214.8 | YES
19 | OK | 5 | 24 | 3 | 13 | 92.3 | 2.6 | 50 | 78.9 | 10.9 | 75.9 | 12.7 | 213.7 | 227.2 | 213.7 | YES
| NG | 17 | 10 | 81 | 23 | 33.9 | 28.49 | 50 | 78.9 | 10.9 | 44.3 | 42.3 | 223.6 | 11.7 | 11.7 | NO
20 | OK | 29 | 28 | 28 | 13 | 99.9 | 3.72 | 95 | 78.9 | 10.9 | 74.5 | 13.5 | 214.9 | 227.1 | 214.9 | YES
21 | OK | 6 | 18 | 18 | 13 | 126.2 | 14.05 | 50 | 78.9 | 10.9 | 62.5 | 21.1 | 214.3 | 225 | 214.3 | YES
22 | OK | 24 | 4 | 3 | 13 | 92.3 | 1.05 | 50 | 78.9 | 10.9 | 77.7 | 11.6 | 213.4 | 227.4 | 213.4 | YES
| NG | 10 | 11 | 81 | 23 | 33.9 | 28.48 | 50 | 78.9 | 10.9 | 44.9 | 18.5 | 223.4 | 209.9 | 209.9 | NO
23 | OK | 28 | 27 | 27 | 13 | 100.3 | 3.72 | 95 | 78.9 | 10.9 | 74.5 | 12.6 | 214.9 | 227.1 | 214.9 | YES
24 | OK | 18 | 19 | 19 | 13 | 134.4 | 12.92 | 50 | 78.9 | 10.9 | 63.8 | 20.3 | 214.2 | 224.9 | 214.2 | YES
| NG | 11 | 30 | 81 | 23 | 33.9 | 27.38 | 50 | 78.9 | 10.9 | 46.2 | 18.5 | 223.4 | 209.9 | 209.9 | NO
25 | OK | 27 | 26 | 26 | 13 | 101.9 | 0.31 | 95 | 78.9 | 10.9 | 78.6 | 11.1 | 213.4 | 227.4 | 213.4 | YES
26 | OK | 19 | 20 | 20 | 13 | 142.5 | 11.19 | 50 | 78.9 | 10.9 | 65.8 | 19 | 214.2 | 225.7 | 214.2 | YES
| NG | 30 | 12 | 81 | 23 | 33.9 | 27.38 | 50 | 78.9 | 10.9 | 46.2 | 18.5 | 223.4 | 209.9 | 209.9 | NO
27 | OK | 26 | 9 | 9 | 13 | 103.4 | 0.1 | 95 | 78.9 | 10.9 | 78.8 | 10.9 | 213.4 | 227.4 | 213.4 | YES
28 | OK | 20 | 21 | 21 | 13 | 154.2 | 8.5 | 50 | 78.9 | 10.9 | 68.9 | 17 | 213.8 | 226.9 | 213.8 | YES
| NG | 12 | 13 | 81 | 23 | 33.9 | 26.15 | 50 | 78.9 | 10.9 | 47.6 | 18.5 | 223.4 | 209.9 | 209.9 | NO
29 | OK | 21 | 22 | 22 | 13 | 182.5 | 4.98 | 50 | 78.9 | 10.9 | 73 | 14.5 | 213.9 | 226.7 | 213.9 | YES
| NG | 13 | 31 | 81 | 23 | 33.9 | 25.25 | 50 | 78.9 | 10.9 | 47.6 | 18.5 | 223.4 | 209.9 | 209.9 | NO
30 | OK | 31 | 32 | 81 | 23 | 33.9 | 22.41 | 50 | 78.9 | 10.9 | 52 | 17.1 | 223.1 | 212.9 | 212.9 | YES
31 | OK | 32 | 35 | 81 | 23 | 33.9 | 21.49 | 50 | 78.9 | 10.9 | 53 | 16.7 | 223 | 213.7 | 213.7 | YES
32 | OK | 35 | 44 | 81 | 23 | 33.9 | 18.5 | 50 | 78.9 | 10.9 | 56.5 | 15.6 | 222.2 | 215.9 | 215.9 | YES
33 | OK | 44 | 41 | 81 | 23 | 33.9 | 18.5 | 50 | 78.9 | 10.9 | 56.5 | 15.6 | 222.2 | 215.9 | 215.9 | YES
34 | OK | 41 | 42 | 81 | 23 | 33.9 | 6.23 | 50 | 78.9 | 10.9 | 71.3 | 12.7 | 216.6 | 223.8 | 216.6 | YES
35 | ** OPTIMAL ** | 41 | 43 | 43 | 23 | 186 | 10.06 | 50 | 78.9 | 10.9 | 66.6 | 18.3 | 219.6 | 220.9 | 219.6 | YES
36 | OK | 41 | 59 | 38 | 18 | 92.4 | 2.11 | 50 | 78.9 | 10.9 | 76.2 | 12.4 | 212.7 | 227.4 | 212.7 | YES
37 | OK | 42 | 47 | 81 | 23 | 33.9 | 3.93 | 50 | 78.9 | 10.9 | 74.1 | 11.6 | 214.6 | 225.9 | 214.6 | YES
38 | OK | 42 | 67 | 53 | 21 | 125.8 | 2.3 | 50 | 78.9 | 10.9 | 76.1 | 12.5 | 215.4 | 227.2 | 215.4 | YES
39 | OK | 59 | 58 | 38 | 18 | 92.4 | 2.11 | 50 | 78.9 | 10.9 | 76.4 | 12.4 | 212.7 | 227.4 | 212.7 | YES
40 | OK | 47 | 48 | 65 | 28 | 116.5 | 3.9 | 50 | 78.9 | 10.9 | 74.1 | 13.7 | 214.5 | 227.2 | 214.5 | YES
41 | OK | 47 | 49 | 81 | 23 | 33.9 | 0.03 | 50 | 78.9 | 10.9 | 78.9 | 10.9 | 213.4 | 227.3 | 213.4 | YES
42 | OK | 67 | 66 | 53 | 21 | 125.8 | 0.83 | 50 | 78.9 | 10.9 | 77.9 | 11.5 | 214.1 | 227.3 | 214.1 | YES
43 | OK | 58 | 38 | 38 | 18 | 92.4 | 0.11 | 50 | 78.9 | 10.9 | 78.8 | 10.9 | 213.4 | 227.4 | 213.4 | YES
44 | OK | 48 | 68 | 65 | 28 | 116.5 | 2.63 | 50 | 78.9 | 10.9 | 75.7 | 12.8 | 214.5 | 227.3 | 214.5 | YES
45 | OK | 49 | 70 | 81 | 23 | 33.9 | 0.03 | 50 | 78.9 | 10.9 | 78.9 | 10.9 | 213.4 | 227.3 | 213.4 | YES
46 | OK | 66 | 53 | 53 | 21 | 125.8 | 0.49 | 50 | 78.9 | 10.9 | 78.3 | 11.2 | 214.2 | 227.3 | 214.2 | YES
47 | OK | 68 | 69 | 65 | 28 | 116.5 | 1.9 | 50 | 78.9 | 10.9 | 76.6 | 12.2 | 213.3 | 227.4 | 213.3 | YES
48 | OK | 70 | 71 | 81 | 23 | 33.9 | 0.03 | 50 | 78.9 | 10.9 | 78.9 | 10.9 | 213.4 | 227.3 | 213.4 | YES
49 | OK | 69 | 64 | 65 | 28 | 116.5 | 0.03 | 50 | 78.9 | 10.9 | 78.9 | 10.9 | 213.4 | 227.4 | 213.4 | YES
50 | OK | 71 | 81 | 81 | 23 | 33.9 | 0.02 | 50 | 78.9 | 10.9 | 78.9 | 10.9 | 213.4 | 227.4 | 213.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-025728
TR_B (available) | 38-023260
TR_A Rated kVA | 100
TR_B Rated kVA | 160
TR_A Baseline Loading% | 78.9
TR_B Baseline Loading% | 10.9
Total Scenarios Evaluated | 60
Feasible Scenarios | 50
--- Optimal Solution ---
Switch Parent Node | 41
Switch Child Node | 43
Tie Node (TR_A side) | 43
Tie Node (TR_B side) | 23
Tie Line Distance (m) | 186
Load Transferred (kW) | 10.06
TR_A Loading After (%) | 66.6
TR_B Loading After (%) | 18.3
Minimum Voltage (V) | 219.6