## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 34 | 55 | 61 | 17 | 143.8 | 37.56 | 50 | 78.9 | 8.9 | 34.5 | 37.6 | 224.4 | 203.5 | 203.5 | NO
| NG | 55 | 50 | 61 | 17 | 143.8 | 37.56 | 50 | 78.9 | 8.9 | 34.5 | 37.6 | 224.4 | 203.5 | 203.5 | NO
| NG | 50 | 51 | 61 | 17 | 143.8 | 37.56 | 50 | 78.9 | 8.9 | 34.5 | 37.6 | 224.4 | 203.5 | 203.5 | NO
| NG | 51 | 77 | 61 | 17 | 143.8 | 37.54 | 50 | 78.9 | 8.9 | 34.5 | 37.6 | 224.4 | 203.5 | 203.5 | NO
| NG | 77 | 7 | 61 | 17 | 143.8 | 37.54 | 50 | 78.9 | 8.9 | 34.5 | 37.6 | 224.4 | 203.5 | 203.5 | NO
| NG | 7 | 8 | 61 | 17 | 143.8 | 37.33 | 50 | 78.9 | 8.9 | 34.8 | 37.4 | 224.4 | 203.5 | 203.5 | NO
| NG | 8 | 25 | 61 | 17 | 143.8 | 37.15 | 50 | 78.9 | 8.9 | 35 | 37.2 | 224.3 | 203.4 | 203.4 | NO
| NG | 25 | 16 | 61 | 17 | 143.8 | 36.62 | 50 | 78.9 | 8.9 | 35.6 | 36.8 | 224.2 | 203.3 | 203.3 | NO
1 | OK | 16 | 17 | 61 | 17 | 143.8 | 29.49 | 50 | 78.9 | 8.9 | 43.8 | 30.9 | 223.7 | 214.4 | 214.4 | YES
| NG | 17 | 10 | 61 | 17 | 143.8 | 28.49 | 50 | 78.9 | 8.9 | 44.3 | 3860.1 | 223.6 | 7.6 | 7.6 | NO
2 | OK | 10 | 11 | 61 | 17 | 143.8 | 28.48 | 50 | 78.9 | 8.9 | 44.9 | 30.1 | 223.4 | 217.2 | 217.2 | YES
3 | OK | 11 | 30 | 61 | 17 | 143.8 | 27.38 | 50 | 78.9 | 8.9 | 46.2 | 29.2 | 223.4 | 216.6 | 216.6 | YES
4 | OK | 30 | 12 | 61 | 17 | 143.8 | 27.38 | 50 | 78.9 | 8.9 | 46.2 | 29.2 | 223.4 | 216.6 | 216.6 | YES
5 | OK | 12 | 13 | 61 | 17 | 143.8 | 26.15 | 50 | 78.9 | 8.9 | 47.6 | 28.3 | 223.4 | 216.4 | 216.4 | YES
6 | OK | 13 | 31 | 61 | 17 | 143.8 | 25.25 | 50 | 78.9 | 8.9 | 47.6 | 27.6 | 223.4 | 216.3 | 216.3 | YES
7 | OK | 31 | 32 | 61 | 17 | 143.8 | 22.41 | 50 | 78.9 | 8.9 | 52 | 25.4 | 223.1 | 219.4 | 219.4 | YES
8 | OK | 32 | 35 | 61 | 17 | 143.8 | 21.49 | 50 | 78.9 | 8.9 | 53 | 24.4 | 223 | 220.2 | 220.2 | YES
9 | OK | 35 | 44 | 61 | 17 | 143.8 | 18.5 | 50 | 78.9 | 8.9 | 56.5 | 22.4 | 222.2 | 222.2 | 222.2 | YES
10 | OK | 35 | 45 | 57 | 17 | 182.2 | 1.07 | 50 | 78.9 | 8.9 | 77.6 | 8.9 | 214.7 | 226.1 | 214.7 | YES
11 | ** OPTIMAL ** | 44 | 41 | 61 | 17 | 143.8 | 18.5 | 50 | 78.9 | 8.9 | 56.5 | 22.4 | 222.2 | 222.2 | 222.2 | YES
12 | OK | 45 | 56 | 57 | 17 | 182.2 | 0.1 | 50 | 78.9 | 8.9 | 78.8 | 8.9 | 213.3 | 226.1 | 213.3 | YES
13 | OK | 41 | 43 | 61 | 17 | 143.8 | 10.06 | 50 | 78.9 | 8.9 | 66.6 | 16.1 | 219.6 | 225.2 | 219.6 | YES
14 | OK | 56 | 57 | 57 | 17 | 182.2 | 0.1 | 50 | 78.9 | 8.9 | 78.8 | 8.9 | 213.3 | 226.1 | 213.3 | YES
15 | OK | 43 | 60 | 61 | 17 | 143.8 | 7.77 | 50 | 78.9 | 8.9 | 69.4 | 14.5 | 217.8 | 225.8 | 217.8 | YES
16 | OK | 60 | 61 | 61 | 17 | 143.8 | 7.09 | 50 | 78.9 | 8.9 | 70.2 | 14 | 217.8 | 225.8 | 217.8 | YES
17 | OK | 61 | 62 | 62 | 17 | 149 | 5.66 | 50 | 78.9 | 8.9 | 71.9 | 12.9 | 216.7 | 225.9 | 216.7 | YES
18 | OK | 61 | 39 | 39 | 17 | 143.9 | 1.43 | 50 | 78.9 | 8.9 | 77.1 | 9.9 | 214.6 | 226 | 214.6 | YES
19 | OK | 62 | 63 | 63 | 17 | 183.3 | 4.36 | 50 | 78.9 | 8.9 | 73.5 | 12 | 216.8 | 225.9 | 216.8 | YES
20 | OK | 39 | 40 | 40 | 17 | 149.5 | 0.29 | 50 | 78.9 | 8.9 | 78.6 | 9.1 | 213.3 | 226.1 | 213.3 | YES
21 | OK | 63 | 46 | 46 | 17 | 207.5 | 2.53 | 50 | 78.9 | 8.9 | 75.8 | 10.7 | 214.8 | 226 | 214.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-025728
TR_B (available) | 56-002662
TR_A Rated kVA | 100
TR_B Rated kVA | 160
TR_A Baseline Loading% | 78.9
TR_B Baseline Loading% | 8.9
Total Scenarios Evaluated | 30
Feasible Scenarios | 21
--- Optimal Solution ---
Switch Parent Node | 44
Switch Child Node | 41
Tie Node (TR_A side) | 61
Tie Node (TR_B side) | 17
Tie Line Distance (m) | 143.8
Load Transferred (kW) | 18.5
TR_A Loading After (%) | 56.5
TR_B Loading After (%) | 22.4
Minimum Voltage (V) | 222.2