## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 34 | 33 | 80 | 33 | 22.2 | 29.81 | 50 | 78.9 | 36.1 | 44.4 | 71.3 | 215.5 | 217.1 | 215.5 | YES
| NG | 34 | 55 | 55 | 32 | 55.2 | 37.56 | 50 | 78.9 | 36.1 | 34.5 | 82.3 | 224.4 | 201.8 | 201.8 | NO
2 | OK | 33 | 76 | 80 | 33 | 22.2 | 29.81 | 50 | 78.9 | 36.1 | 44.4 | 71.3 | 215.5 | 217.1 | 215.5 | YES
| NG | 55 | 50 | 50 | 32 | 61.8 | 37.56 | 50 | 78.9 | 36.1 | 34.5 | 82.3 | 224.4 | 201.7 | 201.7 | NO
3 | OK | 76 | 75 | 80 | 33 | 22.2 | 27.67 | 50 | 78.9 | 36.1 | 46.8 | 68.8 | 215.5 | 217 | 215.5 | YES
4 | OK | 76 | 78 | 78 | 32 | 36 | 2.14 | 50 | 78.9 | 36.1 | 76.5 | 38.6 | 213.3 | 224.3 | 213.3 | YES
| NG | 50 | 51 | 51 | 32 | 79.6 | 37.56 | 50 | 78.9 | 36.1 | 34.5 | 82.4 | 224.4 | 201.4 | 201.4 | NO
5 | OK | 75 | 74 | 80 | 33 | 22.2 | 27.67 | 50 | 78.9 | 36.1 | 46.8 | 68.8 | 215.5 | 217 | 215.5 | YES
| NG | 51 | 77 | 77 | 32 | 82.8 | 37.54 | 50 | 78.9 | 36.1 | 34.5 | 82.3 | 224.4 | 201.3 | 201.3 | NO
6 | OK | 74 | 54 | 80 | 33 | 22.2 | 27.67 | 50 | 78.9 | 36.1 | 46.8 | 67.9 | 215.5 | 216.9 | 215.5 | YES
| NG | 77 | 7 | 7 | 32 | 89.6 | 37.54 | 50 | 78.9 | 36.1 | 34.5 | 82.3 | 224.4 | 201.6 | 201.6 | NO
7 | OK | 54 | 80 | 80 | 33 | 22.2 | 1.15 | 50 | 78.9 | 36.1 | 77.6 | 37.5 | 213.4 | 224.2 | 213.4 | YES
8 | OK | 54 | 72 | 72 | 32 | 33.2 | 25.78 | 50 | 78.9 | 36.1 | 49 | 66.5 | 215.5 | 217.3 | 215.5 | YES
| NG | 7 | 8 | 8 | 32 | 114.4 | 37.33 | 50 | 78.9 | 36.1 | 34.8 | 82 | 224.4 | 201.8 | 201.8 | NO
9 | OK | 72 | 73 | 73 | 32 | 38.1 | 25.78 | 50 | 78.9 | 36.1 | 49 | 66.5 | 215.5 | 217.3 | 215.5 | YES
| NG | 8 | 25 | 9 | 32 | 133.3 | 37.15 | 50 | 78.9 | 36.1 | 35 | 81.8 | 224.3 | 201.5 | 201.5 | NO
10 | OK | 73 | 52 | 52 | 32 | 77.3 | 22.57 | 50 | 78.9 | 36.1 | 52.7 | 62.7 | 215.1 | 218.6 | 215.1 | YES
| NG | 25 | 16 | 9 | 32 | 133.3 | 36.62 | 50 | 78.9 | 36.1 | 35.6 | 81.2 | 224.2 | 201.5 | 201.5 | NO
11 | OK | 52 | 5 | 3 | 32 | 94.5 | 20.1 | 50 | 78.9 | 36.1 | 55.5 | 59.8 | 215.1 | 218 | 215.1 | YES
| NG | 16 | 17 | 17 | 32 | 147.9 | 29.49 | 50 | 78.9 | 36.1 | 43.8 | 72.1 | 223.7 | 207.4 | 207.4 | NO
12 | ** OPTIMAL ** | 16 | 29 | 9 | 32 | 133.3 | 7.13 | 50 | 78.9 | 36.1 | 70.5 | 44.4 | 216.1 | 221.9 | 216.1 | YES
13 | OK | 5 | 6 | 6 | 32 | 111.5 | 17.5 | 50 | 78.9 | 36.1 | 58.5 | 56.7 | 214.8 | 219.9 | 214.8 | YES
14 | OK | 5 | 24 | 3 | 32 | 94.5 | 2.6 | 50 | 78.9 | 36.1 | 75.9 | 39.1 | 213.7 | 223.7 | 213.7 | YES
| NG | 17 | 10 | 10 | 32 | 149.1 | 28.49 | 50 | 78.9 | 36.1 | 44.3 | 548.8 | 223.6 | 7.6 | 7.6 | NO
15 | OK | 29 | 28 | 9 | 32 | 133.3 | 3.72 | 50 | 78.9 | 36.1 | 74.5 | 40.4 | 214.9 | 223.3 | 214.9 | YES
16 | OK | 6 | 18 | 18 | 32 | 123.7 | 14.05 | 50 | 78.9 | 36.1 | 62.5 | 52.6 | 214.3 | 222.4 | 214.3 | YES
17 | OK | 24 | 4 | 3 | 32 | 94.5 | 1.05 | 50 | 78.9 | 36.1 | 77.7 | 37.3 | 213.4 | 224.3 | 213.4 | YES
18 | OK | 28 | 27 | 9 | 32 | 133.3 | 3.72 | 50 | 78.9 | 36.1 | 74.5 | 38.9 | 214.9 | 223.3 | 214.9 | YES
19 | OK | 18 | 19 | 19 | 32 | 133.8 | 12.92 | 50 | 78.9 | 36.1 | 63.8 | 51.2 | 214.2 | 222.8 | 214.2 | YES
20 | OK | 27 | 26 | 9 | 32 | 133.3 | 0.31 | 50 | 78.9 | 36.1 | 78.6 | 36.5 | 213.4 | 224.3 | 213.4 | YES
21 | OK | 19 | 20 | 20 | 32 | 144 | 11.19 | 50 | 78.9 | 36.1 | 65.8 | 49.2 | 214.2 | 222.5 | 214.2 | YES
22 | OK | 26 | 9 | 9 | 32 | 133.3 | 0.1 | 50 | 78.9 | 36.1 | 78.8 | 36.2 | 213.4 | 224.3 | 213.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-025728
TR_B (available) | 62-001605
TR_A Rated kVA | 100
TR_B Rated kVA | 100
TR_A Baseline Loading% | 78.9
TR_B Baseline Loading% | 36.1
Total Scenarios Evaluated | 32
Feasible Scenarios | 22
--- Optimal Solution ---
Switch Parent Node | 16
Switch Child Node | 29
Tie Node (TR_A side) | 9
Tie Node (TR_B side) | 32
Tie Line Distance (m) | 133.3
Load Transferred (kW) | 7.13
TR_A Loading After (%) | 70.5
TR_B Loading After (%) | 44.4
Minimum Voltage (V) | 216.1