## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 34 | 33 | 2 | 32 | 107.1 | 29.81 | 50 | 78.9 | 20.9 | 44.4 | 43.1 | 215.5 | 135.6 | 135.6 | NO
| NG | 34 | 55 | 46 | 32 | 12.2 | 37.56 | 50 | 78.9 | 20.9 | 34.5 | 26.4 | 224.4 | 203.2 | 203.2 | NO
| NG | 33 | 76 | 2 | 32 | 107.1 | 29.81 | 50 | 78.9 | 20.9 | 44.4 | 43.1 | 215.5 | 135.6 | 135.6 | NO
| NG | 55 | 50 | 46 | 32 | 12.2 | 37.56 | 50 | 78.9 | 20.9 | 34.5 | 26.4 | 224.4 | 203.2 | 203.2 | NO
| NG | 76 | 75 | 2 | 32 | 107.1 | 27.67 | 50 | 78.9 | 20.9 | 46.8 | 39.7 | 215.5 | 151 | 151 | NO
| NG | 50 | 51 | 46 | 32 | 12.2 | 37.56 | 50 | 78.9 | 20.9 | 34.5 | 26.4 | 224.4 | 203.2 | 203.2 | NO
| NG | 75 | 74 | 2 | 32 | 107.1 | 27.67 | 50 | 78.9 | 20.9 | 46.8 | 39.7 | 215.5 | 151 | 151 | NO
| NG | 51 | 77 | 46 | 32 | 12.2 | 37.54 | 50 | 78.9 | 20.9 | 34.5 | 26.4 | 224.4 | 203.2 | 203.2 | NO
| NG | 74 | 54 | 2 | 32 | 107.1 | 27.67 | 50 | 78.9 | 20.9 | 46.8 | 38.8 | 215.5 | 155.1 | 155.1 | NO
| NG | 77 | 7 | 46 | 32 | 12.2 | 37.54 | 50 | 78.9 | 20.9 | 34.5 | 26.4 | 224.4 | 203.2 | 203.2 | NO
| NG | 54 | 72 | 2 | 32 | 107.1 | 25.78 | 50 | 78.9 | 20.9 | 49 | 37.4 | 215.5 | 161 | 161 | NO
| NG | 7 | 8 | 46 | 32 | 12.2 | 37.33 | 50 | 78.9 | 20.9 | 34.8 | 26.4 | 224.4 | 203.2 | 203.2 | NO
| NG | 72 | 73 | 2 | 32 | 107.1 | 25.78 | 50 | 78.9 | 20.9 | 49 | 37.4 | 215.5 | 161 | 161 | NO
| NG | 8 | 25 | 46 | 32 | 12.2 | 37.15 | 50 | 78.9 | 20.9 | 35 | 26.4 | 224.3 | 203.3 | 203.3 | NO
| NG | 73 | 52 | 2 | 32 | 107.1 | 22.57 | 50 | 78.9 | 20.9 | 52.7 | 34.4 | 215.1 | 174.3 | 174.3 | NO
| NG | 25 | 16 | 46 | 32 | 12.2 | 36.62 | 50 | 78.9 | 20.9 | 35.6 | 26.4 | 224.2 | 203.3 | 203.3 | NO
| NG | 52 | 5 | 2 | 32 | 107.1 | 20.1 | 50 | 78.9 | 20.9 | 55.5 | 32.4 | 215.1 | 182.4 | 182.4 | NO
| NG | 16 | 17 | 46 | 32 | 12.2 | 29.49 | 50 | 78.9 | 20.9 | 43.8 | 26 | 223.7 | 205.5 | 205.5 | NO
| NG | 5 | 6 | 2 | 32 | 107.1 | 17.5 | 50 | 78.9 | 20.9 | 58.5 | 30.6 | 214.8 | 190.1 | 190.1 | NO
| NG | 17 | 10 | 46 | 32 | 12.2 | 28.49 | 50 | 78.9 | 20.9 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 20.9% (degenerate)
| NG | 6 | 18 | 2 | 32 | 107.1 | 14.05 | 50 | 78.9 | 20.9 | 62.5 | 28.3 | 214.3 | 199 | 199 | NO
| NG | 10 | 11 | 46 | 32 | 12.2 | 28.48 | 50 | 78.9 | 20.9 | 44.9 | 26 | 223.4 | 205.5 | 205.5 | NO
| NG | 18 | 19 | 2 | 32 | 107.1 | 12.92 | 50 | 78.9 | 20.9 | 63.8 | 27.6 | 214.2 | 201.7 | 201.7 | NO
| NG | 11 | 30 | 46 | 32 | 12.2 | 27.38 | 50 | 78.9 | 20.9 | 46.2 | 25.3 | 223.4 | 208.6 | 208.6 | NO
| NG | 19 | 20 | 2 | 32 | 107.1 | 11.19 | 50 | 78.9 | 20.9 | 65.8 | 26.6 | 214.2 | 205.6 | 205.6 | NO
| NG | 30 | 12 | 46 | 32 | 12.2 | 27.38 | 50 | 78.9 | 20.9 | 46.2 | 25.3 | 223.4 | 208.6 | 208.6 | NO
1 | OK | 20 | 21 | 2 | 32 | 107.1 | 8.5 | 50 | 78.9 | 20.9 | 68.9 | 25.1 | 213.8 | 211.3 | 211.3 | YES
| NG | 12 | 13 | 46 | 32 | 12.2 | 26.15 | 50 | 78.9 | 20.9 | 47.6 | 25.3 | 223.4 | 208.6 | 208.6 | NO
2 | OK | 21 | 22 | 2 | 32 | 107.1 | 4.98 | 50 | 78.9 | 20.9 | 73 | 23.3 | 213.9 | 218 | 213.9 | YES
| NG | 13 | 31 | 46 | 32 | 12.2 | 25.25 | 50 | 78.9 | 20.9 | 47.6 | 25.3 | 223.4 | 208.6 | 208.6 | NO
3 | OK | 22 | 1 | 2 | 32 | 107.1 | 2.09 | 50 | 78.9 | 20.9 | 76.5 | 21.9 | 213.9 | 223 | 213.9 | YES
4 | OK | 31 | 32 | 46 | 32 | 12.2 | 22.41 | 50 | 78.9 | 20.9 | 52 | 24.7 | 223.1 | 211.3 | 211.3 | YES
5 | OK | 1 | 2 | 2 | 32 | 107.1 | 2.09 | 50 | 78.9 | 20.9 | 76.5 | 21.9 | 213.9 | 223 | 213.9 | YES
6 | OK | 32 | 35 | 46 | 32 | 12.2 | 21.49 | 50 | 78.9 | 20.9 | 53 | 24.5 | 223 | 212.3 | 212.3 | YES
7 | OK | 2 | 23 | 23 | 32 | 107.3 | 0.64 | 50 | 78.9 | 20.9 | 78.2 | 21.2 | 213.5 | 225.1 | 213.5 | YES
8 | OK | 35 | 44 | 46 | 32 | 12.2 | 18.5 | 50 | 78.9 | 20.9 | 56.5 | 24.2 | 222.2 | 213.3 | 213.3 | YES
9 | OK | 35 | 45 | 57 | 32 | 138.9 | 1.07 | 50 | 78.9 | 20.9 | 77.6 | 20.9 | 214.7 | 225.8 | 214.7 | YES
10 | OK | 35 | 37 | 36 | 32 | 135.5 | 1.52 | 50 | 78.9 | 20.9 | 77.1 | 21 | 213.6 | 225.5 | 213.6 | YES
11 | OK | 44 | 41 | 46 | 32 | 12.2 | 18.5 | 50 | 78.9 | 20.9 | 56.5 | 24.2 | 222.2 | 213.3 | 213.3 | YES
12 | OK | 45 | 56 | 57 | 32 | 138.9 | 0.1 | 50 | 78.9 | 20.9 | 78.8 | 20.9 | 213.3 | 225.8 | 213.3 | YES
| NG | 37 | 36 | 36 | 32 | 135.5 | 1.25 | 50 | 78.9 | 20.9 | 13.4 | 20.9 | 15 | 225.9 | 15 | NO
13 | ** OPTIMAL ** | 41 | 43 | 46 | 32 | 12.2 | 10.06 | 50 | 78.9 | 20.9 | 66.6 | 22.4 | 219.6 | 221.3 | 219.6 | YES
14 | OK | 41 | 59 | 59 | 32 | 197.6 | 2.11 | 50 | 78.9 | 20.9 | 76.2 | 21.8 | 212.7 | 222.2 | 212.7 | YES
15 | OK | 56 | 57 | 57 | 32 | 138.9 | 0.1 | 50 | 78.9 | 20.9 | 78.8 | 20.9 | 213.3 | 225.9 | 213.3 | YES
16 | OK | 43 | 60 | 46 | 32 | 12.2 | 7.77 | 50 | 78.9 | 20.9 | 69.4 | 22 | 217.8 | 223 | 217.8 | YES
17 | OK | 60 | 61 | 46 | 32 | 12.2 | 7.09 | 50 | 78.9 | 20.9 | 70.2 | 22 | 217.8 | 223 | 217.8 | YES
18 | OK | 61 | 62 | 46 | 32 | 12.2 | 5.66 | 50 | 78.9 | 20.9 | 71.9 | 21.8 | 216.7 | 223.8 | 216.7 | YES
19 | OK | 61 | 39 | 39 | 48 | 157.3 | 1.43 | 50 | 78.9 | 20.9 | 77.1 | 21.1 | 214.6 | 225.2 | 214.6 | YES
20 | OK | 62 | 63 | 46 | 32 | 12.2 | 4.36 | 50 | 78.9 | 20.9 | 73.5 | 21.8 | 216.8 | 223.8 | 216.8 | YES
21 | OK | 39 | 40 | 40 | 48 | 191.9 | 0.29 | 50 | 78.9 | 20.9 | 78.6 | 20.9 | 213.3 | 225.9 | 213.3 | YES
22 | OK | 63 | 46 | 46 | 32 | 12.2 | 2.53 | 50 | 78.9 | 20.9 | 75.8 | 21.3 | 214.8 | 224.9 | 214.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-025728
TR_B (available) | 66-016972
TR_A Rated kVA | 100
TR_B Rated kVA | 250
TR_A Baseline Loading% | 78.9
TR_B Baseline Loading% | 20.9
Total Scenarios Evaluated | 51
Feasible Scenarios | 22
--- Optimal Solution ---
Switch Parent Node | 41
Switch Child Node | 43
Tie Node (TR_A side) | 46
Tie Node (TR_B side) | 32
Tie Line Distance (m) | 12.2
Load Transferred (kW) | 10.06
TR_A Loading After (%) | 66.6
TR_B Loading After (%) | 22.4
Minimum Voltage (V) | 219.6