## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 3 | 0 | 76 | 2 | 22.8 | 35.47 | 50 | 80.7 | 7.1 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 0 | 1 | 76 | 2 | 22.8 | 34.7 | 50 | 80.7 | 7.1 | [5 empty] | NO | TR_B sim: not converged
| NG | 1 | 61 | 76 | 2 | 22.8 | 31.95 | 50 | 80.7 | 7.1 | [5 empty] | NO | TR_B sim: not converged
| NG | 61 | 64 | 76 | 2 | 22.8 | 29.73 | 50 | 80.7 | 7.1 | 42.2 | 29.8 | 217.8 | 123.3 | 123.3 | NO
| NG | 64 | 48 | 76 | 2 | 22.8 | 29.73 | 50 | 80.7 | 7.1 | 42.2 | 29.8 | 217.8 | 123.3 | 123.3 | NO
| NG | 48 | 38 | 76 | 2 | 22.8 | 27.19 | 50 | 80.7 | 7.1 | 0 | 25.4 | 6 | 147.9 | 6 | NO
| NG | 38 | 39 | 76 | 2 | 22.8 | 25.82 | 50 | 80.7 | 7.1 | 46.7 | 23.7 | 217.5 | 157.2 | 157.2 | NO
| NG | 39 | 42 | 76 | 2 | 22.8 | 25.24 | 50 | 80.7 | 7.1 | 47.4 | 23.1 | 217.5 | 161 | 161 | NO
| NG | 42 | 43 | 76 | 2 | 22.8 | 23.99 | 50 | 80.7 | 7.1 | 48.8 | 21.9 | 217.2 | 167.4 | 167.4 | NO
| NG | 43 | 59 | 76 | 2 | 22.8 | 23.99 | 50 | 80.7 | 7.1 | 48.8 | 21.9 | 217.2 | 167.4 | 167.4 | NO
| NG | 59 | 51 | 76 | 2 | 22.8 | 23.99 | 50 | 80.7 | 7.1 | 48.8 | 21.9 | 217.2 | 167.4 | 167.4 | NO
| NG | 51 | 52 | 76 | 2 | 22.8 | 22.12 | 50 | 80.7 | 7.1 | 51 | 20.3 | 217.2 | 175.6 | 175.6 | NO
| NG | 52 | 49 | 76 | 2 | 22.8 | 20.23 | 50 | 80.7 | 7.1 | 53.2 | 18.8 | 217.2 | 183.1 | 183.1 | NO
| NG | 49 | 50 | 76 | 2 | 22.8 | 19.55 | 50 | 80.7 | 7.1 | 54 | 18.3 | 217.1 | 185.5 | 185.5 | NO
| NG | 50 | 54 | 76 | 2 | 22.8 | 17.23 | 50 | 80.7 | 7.1 | 56.7 | 16.7 | 217.1 | 192.9 | 192.9 | NO
| NG | 54 | 55 | 76 | 2 | 22.8 | 17.23 | 50 | 80.7 | 7.1 | 56.7 | 16.3 | 217.1 | 194.5 | 194.5 | NO
| NG | 55 | 73 | 76 | 2 | 22.8 | 15.1 | 50 | 80.7 | 7.1 | 59.2 | 15.3 | 216.8 | 197.3 | 197.3 | NO
| NG | 73 | 7 | 76 | 2 | 22.8 | 14.58 | 50 | 80.7 | 7.1 | 59.8 | 15 | 216.8 | 197.8 | 197.8 | NO
| NG | 7 | 8 | 76 | 2 | 22.8 | 12.29 | 50 | 80.7 | 7.1 | 62.6 | 13.7 | 216.8 | 200.1 | 200.1 | NO
| NG | 8 | 62 | 76 | 2 | 22.8 | 11.88 | 50 | 80.7 | 7.1 | 63.1 | 13.4 | 216.8 | 200.5 | 200.5 | NO
| NG | 62 | 5 | 76 | 2 | 22.8 | 9.31 | 50 | 80.7 | 7.1 | 66.3 | 12 | 211.8 | 202.9 | 202.9 | NO
| NG | 5 | 6 | 76 | 2 | 22.8 | 9.2 | 50 | 80.7 | 7.1 | 66.4 | 11.9 | 211.9 | 203 | 203 | NO
| NG | 6 | 47 | 76 | 2 | 22.8 | 9.2 | 50 | 80.7 | 7.1 | 66.4 | 11.9 | 211.9 | 203 | 203 | NO
| NG | 47 | 74 | 76 | 2 | 22.8 | 9.15 | 50 | 80.7 | 7.1 | 66.5 | 11.9 | 211.7 | 203 | 203 | NO
| NG | 74 | 76 | 76 | 2 | 22.8 | 0.89 | 50 | 80.7 | 7.1 | 78.9 | 7.5 | 179.4 | 210.3 | 179.4 | NO
1 | ** OPTIMAL ** | 74 | 75 | 75 | 3 | 36 | 8.26 | 50 | 80.7 | 7.1 | 67.6 | 7.1 | 211.9 | 211 | 211 | YES
| NG | 76 | 77 | 77 | 2 | 23.1 | 0.89 | 50 | 80.7 | 7.1 | 78.9 | 7.5 | 179.4 | 210.3 | 179.4 | NO
| NG | 77 | 78 | 78 | 40 | 25.6 | 0.89 | 50 | 80.7 | 7.1 | 78.9 | 7.1 | 179.4 | 211 | 179.4 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 60-025782
TR_B (available) | 62-001834
TR_A Rated kVA | 100
TR_B Rated kVA | 250
TR_A Baseline Loading% | 80.7
TR_B Baseline Loading% | 7.1
Total Scenarios Evaluated | 28
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 74
Switch Child Node | 75
Tie Node (TR_A side) | 75
Tie Node (TR_B side) | 3
Tie Line Distance (m) | 36
Load Transferred (kW) | 8.26
TR_A Loading After (%) | 67.6
TR_B Loading After (%) | 7.1
Minimum Voltage (V) | 211