## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 3 | 4 | 89 | 8 | 2 | 12.78 | 50 | 80.1 | 6.3 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 3 | 94 | 46 | 8 | 21.7 | 21.86 | 50 | 80.1 | 6.3 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 4 | 5 | 89 | 8 | 2 | 12.18 | 50 | 80.1 | 6.3 | 51.9 | 35.9 | 221 | 214.6 | 214.6 | YES
| NG | 94 | 58 | 46 | 8 | 21.7 | 20.87 | 50 | 80.1 | 6.3 | 31.8 | 80.3 | 224.2 | 196.1 | 196.1 | NO
2 | OK | 5 | 6 | 89 | 8 | 2 | 12.06 | 50 | 80.1 | 6.3 | 52.2 | 35.4 | 220.9 | 214.9 | 214.9 | YES
3 | OK | 58 | 59 | 46 | 8 | 21.7 | 11.14 | 50 | 80.1 | 6.3 | 54.3 | 37.7 | 222.1 | 211.9 | 211.9 | YES
4 | OK | 58 | 95 | 95 | 8 | 150.6 | 6.61 | 50 | 80.1 | 6.3 | 64.3 | 30.4 | 220 | 216.9 | 216.9 | YES
5 | OK | 58 | 45 | 35 | 8 | 144.4 | 2.94 | 50 | 80.1 | 6.3 | 73.3 | 17.7 | 219.9 | 223.5 | 219.9 | YES
6 | OK | 6 | 7 | 7 | 8 | 29.4 | 12.06 | 50 | 80.1 | 6.3 | 52.2 | 35.4 | 220.9 | 215 | 215 | YES
7 | OK | 59 | 60 | 46 | 8 | 21.7 | 4.2 | 50 | 80.1 | 6.3 | 70.3 | 22.9 | 221.2 | 217.6 | 217.6 | YES
8 | OK | 59 | 61 | 61 | 8 | 154.2 | 6.94 | 50 | 80.1 | 6.3 | 64.1 | 20.5 | 219.7 | 224.1 | 219.7 | YES
9 | OK | 95 | 93 | 93 | 8 | 154.1 | 6.26 | 50 | 80.1 | 6.3 | 65.1 | 30.4 | 220 | 216.9 | 216.9 | YES
10 | OK | 45 | 35 | 35 | 8 | 144.4 | 2.94 | 50 | 80.1 | 6.3 | 73.3 | 17.7 | 219.9 | 223.5 | 219.9 | YES
11 | OK | 7 | 8 | 8 | 8 | 38.8 | 11.37 | 50 | 80.1 | 6.3 | 53.8 | 32.7 | 220.9 | 215.2 | 215.2 | YES
12 | OK | 60 | 64 | 46 | 8 | 21.7 | 4.08 | 50 | 80.1 | 6.3 | 70.6 | 22.4 | 221.2 | 218 | 218 | YES
13 | OK | 61 | 65 | 65 | 8 | 200.4 | 6.6 | 50 | 80.1 | 6.3 | 64.9 | 19.1 | 219.5 | 225.1 | 219.5 | YES
14 | OK | 93 | 92 | 92 | 8 | 199.3 | 6.26 | 50 | 80.1 | 6.3 | 65.1 | 30.4 | 220 | 216.9 | 216.9 | YES
15 | OK | 35 | 36 | 36 | 8 | 152.2 | 2.51 | 50 | 80.1 | 6.3 | 74.3 | 16 | 219.6 | 225 | 219.6 | YES
16 | OK | 8 | 84 | 84 | 8 | 43.1 | 10.15 | 50 | 80.1 | 6.3 | 56.6 | 27.8 | 220.5 | 217.5 | 217.5 | YES
17 | OK | 64 | 63 | 46 | 8 | 21.7 | 3.86 | 50 | 80.1 | 6.3 | 71.1 | 21.5 | 221 | 218.6 | 218.6 | YES
18 | OK | 36 | 37 | 37 | 8 | 166.4 | 1.69 | 50 | 80.1 | 6.3 | 76.2 | 12.8 | 219.1 | 227.6 | 219.1 | YES
19 | OK | 84 | 85 | 85 | 8 | 83.4 | 0.84 | 50 | 80.1 | 6.3 | 78.2 | 9.5 | 218.6 | 227.9 | 218.6 | YES
20 | OK | 84 | 10 | 10 | 8 | 58.5 | 9.31 | 50 | 80.1 | 6.3 | 58.5 | 27.7 | 220.5 | 217.5 | 217.5 | YES
21 | OK | 63 | 62 | 46 | 8 | 21.7 | 3.44 | 50 | 80.1 | 6.3 | 72.1 | 19.8 | 220.8 | 219.8 | 219.8 | YES
22 | OK | 37 | 0 | 0 | 8 | 186.8 | 0.62 | 50 | 80.1 | 6.3 | 78.7 | 8.6 | 219 | 228.2 | 219 | YES
23 | OK | 10 | 9 | 9 | 8 | 80.4 | 9.31 | 50 | 80.1 | 6.3 | 58.5 | 27.7 | 220.5 | 217.6 | 217.6 | YES
24 | OK | 62 | 47 | 46 | 8 | 21.7 | 0.13 | 50 | 80.1 | 6.3 | 79.8 | 6.8 | 218.8 | 229.4 | 218.8 | YES
25 | ** OPTIMAL ** | 62 | 48 | 48 | 8 | 46.3 | 3.31 | 50 | 80.1 | 6.3 | 72.4 | 19.3 | 220.8 | 220.6 | 220.6 | YES
26 | OK | 9 | 11 | 11 | 8 | 103.7 | 9.09 | 50 | 80.1 | 6.3 | 59 | 26.9 | 220.5 | 217.6 | 217.6 | YES
27 | OK | 48 | 49 | 49 | 8 | 70.6 | 2.68 | 50 | 80.1 | 6.3 | 73.8 | 16.7 | 220.5 | 222.3 | 220.5 | YES
28 | OK | 11 | 12 | 12 | 8 | 122.6 | 8.62 | 50 | 80.1 | 6.3 | 60.1 | 25.1 | 220.5 | 217.5 | 217.5 | YES
29 | OK | 49 | 68 | 68 | 8 | 94.5 | 2.48 | 50 | 80.1 | 6.3 | 74.3 | 15.9 | 220.4 | 222.8 | 220.4 | YES
30 | OK | 12 | 21 | 21 | 8 | 128.3 | 7.9 | 50 | 80.1 | 6.3 | 61.7 | 22.4 | 220.2 | 219.3 | 219.3 | YES
31 | OK | 68 | 69 | 69 | 8 | 124.2 | 2.02 | 50 | 80.1 | 6.3 | 75.4 | 14.1 | 220.1 | 224.2 | 220.1 | YES
32 | OK | 21 | 20 | 20 | 8 | 152.9 | 2.45 | 50 | 80.1 | 6.3 | 74.4 | 15.9 | 218.5 | 222.3 | 218.5 | YES
33 | OK | 21 | 44 | 25 | 8 | 139.1 | 5.45 | 50 | 80.1 | 6.3 | 67.4 | 28 | 220.2 | 214.3 | 214.3 | YES
34 | OK | 69 | 70 | 70 | 8 | 162.2 | 1.59 | 50 | 80.1 | 6.3 | 76.4 | 12.4 | 219.9 | 225.4 | 219.9 | YES
35 | OK | 20 | 22 | 22 | 8 | 176.6 | 1.87 | 50 | 80.1 | 6.3 | 75.8 | 13.5 | 218.6 | 224.1 | 218.6 | YES
36 | OK | 44 | 24 | 25 | 8 | 139.1 | 0.41 | 50 | 80.1 | 6.3 | 79.2 | 7.8 | 218.6 | 228.9 | 218.6 | YES
37 | OK | 44 | 13 | 13 | 8 | 149.5 | 4.64 | 50 | 80.1 | 6.3 | 68.4 | 20.8 | 220.2 | 220.6 | 220.2 | YES
38 | OK | 70 | 71 | 71 | 8 | 186.7 | 0.9 | 50 | 80.1 | 6.3 | 78 | 9.7 | 219.6 | 227.5 | 219.6 | YES
39 | OK | 22 | 23 | 23 | 8 | 197.1 | 0.79 | 50 | 80.1 | 6.3 | 78.3 | 9.3 | 218.6 | 227.6 | 218.6 | YES
40 | OK | 13 | 14 | 14 | 8 | 181.6 | 4.28 | 50 | 80.1 | 6.3 | 70.1 | 19.4 | 219.8 | 221.8 | 219.8 | YES
41 | OK | 71 | 72 | 72 | 8 | 207.2 | 0.8 | 50 | 80.1 | 6.3 | 78.2 | 9.3 | 219.5 | 227.8 | 219.5 | YES
42 | OK | 14 | 26 | 26 | 8 | 199.4 | 0.92 | 50 | 80.1 | 6.3 | 78 | 9.8 | 218.6 | 227.2 | 218.6 | YES
43 | OK | 14 | 17 | 17 | 8 | 190.3 | 2.85 | 50 | 80.1 | 6.3 | 72.3 | 17.4 | 219.8 | 221.7 | 219.8 | YES
44 | OK | 26 | 27 | 27 | 8 | 201.5 | 0.59 | 50 | 80.1 | 6.3 | 78.8 | 6.3 | 218.6 | 229.5 | 218.6 | YES
45 | OK | 17 | 15 | 15 | 8 | 193.4 | 2.44 | 50 | 80.1 | 6.3 | 74.4 | 15.9 | 219.8 | 221.6 | 219.8 | YES
46 | OK | 15 | 16 | 31 | 7 | 201.3 | 2.44 | 50 | 80.1 | 6.3 | 74.4 | 15.8 | 219.8 | 222.9 | 219.8 | YES
47 | OK | 16 | 28 | 31 | 7 | 201.3 | 1.91 | 50 | 80.1 | 6.3 | 75.6 | 13.7 | 219.6 | 224.6 | 219.6 | YES
48 | OK | 28 | 29 | 31 | 7 | 201.3 | 1.44 | 50 | 80.1 | 6.3 | 76.7 | 11.8 | 219.3 | 226.1 | 219.3 | YES
49 | OK | 29 | 30 | 31 | 7 | 201.3 | 1.32 | 50 | 80.1 | 6.3 | 77 | 11.4 | 219.3 | 226.4 | 219.3 | YES
50 | OK | 30 | 31 | 31 | 7 | 201.3 | 0.43 | 50 | 80.1 | 6.3 | 79.1 | 6.3 | 218.8 | 229.5 | 218.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-027161
TR_B (available) | 51-012985
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 80.1
TR_B Baseline Loading% | 6.3
Total Scenarios Evaluated | 53
Feasible Scenarios | 50
--- Optimal Solution ---
Switch Parent Node | 62
Switch Child Node | 48
Tie Node (TR_A side) | 48
Tie Node (TR_B side) | 8
Tie Line Distance (m) | 46.3
Load Transferred (kW) | 3.31
TR_A Loading After (%) | 72.4
TR_B Loading After (%) | 19.3
Minimum Voltage (V) | 220.6