## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 59 | 58 | 13 | 63 | 2.5 | 24.98 | 95 | 91.2 | 23.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 59 | 35 | 71 | 59 | 59.4 | 52.59 | 50 | 91.2 | 23.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 58 | 6 | 13 | 63 | 2.5 | 24.98 | 95 | 91.2 | 23.2 | 57.6 | 29.3 | 212 | 210.8 | 210.8 | YES
| NG | 35 | 36 | 71 | 59 | 59.4 | 48.87 | 50 | 91.2 | 23.2 | [5 empty] | NO | TR_B sim: not converged
2 | OK | 6 | 9 | 9 | 63 | 62.8 | 20.6 | 50 | 91.2 | 23.2 | 66.9 | 28.2 | 211 | 213.6 | 211 | YES
| NG | 36 | 26 | 71 | 59 | 59.4 | 47.06 | 50 | 91.2 | 23.2 | 35.6 | 3134.5 | 216.3 | 119.7 | 119.7 | NO
3 | OK | 9 | 10 | 10 | 63 | 67.8 | 20.6 | 50 | 91.2 | 23.2 | 66.9 | 28.2 | 211 | 214.9 | 211 | YES
| NG | 26 | 25 | 71 | 59 | 59.4 | 11.63 | 50 | 91.2 | 23.2 | 77.6 | 26.1 | 207.8 | 209.9 | 207.8 | NO
4 | ** OPTIMAL ** | 10 | 15 | 15 | 63 | 86.2 | 19.15 | 50 | 91.2 | 23.2 | 68.5 | 27.8 | 211 | 215.8 | 211 | YES
| NG | 25 | 24 | 71 | 59 | 59.4 | 11.25 | 50 | 91.2 | 23.2 | 78 | 26.1 | 207.8 | 209.9 | 207.8 | NO
| NG | 15 | 8 | 8 | 63 | 88.7 | 12.27 | 50 | 91.2 | 23.2 | 76.5 | 26 | 209.8 | 219.9 | 209.8 | NO
| NG | 8 | 46 | 46 | 63 | 118.1 | 11.71 | 50 | 91.2 | 23.2 | 77.2 | 26 | 209.7 | 220.1 | 209.7 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 60-027164
TR_B (available) | 35-005231
TR_A Rated kVA | 100
TR_B Rated kVA | 500
TR_A Baseline Loading% | 91.2
TR_B Baseline Loading% | 23.2
Total Scenarios Evaluated | 12
Feasible Scenarios | 4
--- Optimal Solution ---
Switch Parent Node | 10
Switch Child Node | 15
Tie Node (TR_A side) | 15
Tie Node (TR_B side) | 63
Tie Line Distance (m) | 86.2
Load Transferred (kW) | 19.15
TR_A Loading After (%) | 68.5
TR_B Loading After (%) | 27.8
Minimum Voltage (V) | 211