## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 19 | 17 | 27 | 8 | 2 | 4.3 | 50 | 0 | 14.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 19 | 29 | 7 | 8 | 60.1 | 15.33 | 50 | 0 | 14.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 17 | 18 | 14 | 8 | 84.5 | 2.33 | 50 | 0 | 14.2 | 0 | 17.1 | 230.9 | 218.4 | 218.4 | YES
2 | OK | 17 | 27 | 27 | 8 | 2 | 1.97 | 50 | 0 | 14.2 | 0 | 16.6 | 230.9 | 219.9 | 219.9 | YES
| NG | 29 | 25 | 25 | 8 | 192 | 14.62 | 50 | 0 | 14.2 | 0 | 37.3 | 230.9 | 162.9 | 162.9 | NO
3 | OK | 29 | 16 | 7 | 8 | 60.1 | 0.71 | 50 | 0 | 14.2 | 0 | 15.1 | 230.9 | 222.3 | 222.3 | YES
4 | OK | 18 | 20 | 14 | 8 | 84.5 | 2.33 | 50 | 0 | 14.2 | 0 | 17.1 | 230.9 | 218.4 | 218.4 | YES
5 | OK | 27 | 6 | 6 | 8 | 34.6 | 1.97 | 50 | 0 | 14.2 | 0 | 16.6 | 230.9 | 219.9 | 219.9 | YES
| NG | 25 | 0 | 0 | 8 | 210.3 | 14.62 | 50 | 0 | 14.2 | 0 | 37.3 | 230.9 | 162.9 | 162.9 | NO
6 | OK | 16 | 7 | 7 | 8 | 60.1 | 0.62 | 50 | 0 | 14.2 | 0 | 15 | 230.9 | 222.5 | 222.5 | YES
7 | OK | 20 | 15 | 14 | 8 | 84.5 | 1.04 | 50 | 0 | 14.2 | 0 | 15.5 | 230.9 | 221.5 | 221.5 | YES
8 | ** OPTIMAL ** | 7 | 24 | 24 | 8 | 68.5 | 0.62 | 50 | 0 | 14.2 | 0 | 15 | 230.9 | 222.5 | 222.5 | YES
9 | OK | 15 | 14 | 14 | 8 | 84.5 | 1.04 | 50 | 0 | 14.2 | 0 | 15.5 | 230.9 | 221.5 | 221.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-028067
TR_B (available) | 65-018542
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 0
TR_B Baseline Loading% | 14.2
Total Scenarios Evaluated | 13
Feasible Scenarios | 9
--- Optimal Solution ---
Switch Parent Node | 7
Switch Child Node | 24
Tie Node (TR_A side) | 24
Tie Node (TR_B side) | 8
Tie Line Distance (m) | 68.5
Load Transferred (kW) | 0.62
TR_A Loading After (%) | 0
TR_B Loading After (%) | 15
Minimum Voltage (V) | 222.5