## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 50 | 42 | 2 | 28 | 67.6 | 15.24 | 50 | 82.4 | 24 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 42 | 16 | 2 | 28 | 67.6 | 15.07 | 50 | 82.4 | 24 | [5 empty] | NO | TR_B sim: not converged
| NG | 16 | 15 | 2 | 28 | 67.6 | 14.62 | 50 | 82.4 | 24 | [5 empty] | NO | TR_B sim: not converged
| NG | 15 | 7 | 2 | 28 | 67.6 | 5.35 | 50 | 82.4 | 24 | 61.2 | 46 | 215.3 | 208.9 | 208.9 | NO
1 | OK | 7 | 31 | 2 | 28 | 67.6 | 4.84 | 50 | 82.4 | 24 | 63.2 | 43.7 | 214.8 | 211.5 | 211.5 | YES
2 | ** OPTIMAL ** | 31 | 6 | 2 | 28 | 67.6 | 4.14 | 50 | 82.4 | 24 | 65.9 | 40.7 | 214.2 | 214.8 | 214.2 | YES
3 | OK | 6 | 5 | 2 | 28 | 67.6 | 3.92 | 50 | 82.4 | 24 | 66.8 | 39.8 | 214 | 215.8 | 214 | YES
4 | OK | 5 | 3 | 2 | 28 | 67.6 | 3.62 | 50 | 82.4 | 24 | 67.9 | 38.5 | 213.7 | 216.9 | 213.7 | YES
5 | OK | 3 | 19 | 2 | 28 | 67.6 | 3.1 | 50 | 82.4 | 24 | 69.9 | 36.3 | 213.2 | 218.9 | 213.2 | YES
6 | OK | 19 | 29 | 2 | 28 | 67.6 | 3.1 | 50 | 82.4 | 24 | 69.9 | 36.3 | 213.2 | 218.9 | 213.2 | YES
7 | OK | 29 | 53 | 2 | 28 | 67.6 | 2.92 | 50 | 82.4 | 24 | 70.6 | 35.6 | 213 | 219.5 | 213 | YES
8 | OK | 53 | 27 | 2 | 28 | 67.6 | 2.92 | 50 | 82.4 | 24 | 70.6 | 35.6 | 213 | 219.5 | 213 | YES
9 | OK | 27 | 28 | 2 | 28 | 67.6 | 2.92 | 50 | 82.4 | 24 | 70.6 | 35.6 | 213 | 219.5 | 213 | YES
10 | OK | 28 | 25 | 2 | 28 | 67.6 | 2.07 | 50 | 82.4 | 24 | 73.9 | 32.2 | 212.3 | 222.1 | 212.3 | YES
11 | OK | 25 | 26 | 2 | 28 | 67.6 | 2.07 | 50 | 82.4 | 24 | 74 | 32.2 | 212.2 | 222.1 | 212.2 | YES
12 | OK | 26 | 0 | 2 | 28 | 67.6 | 2.07 | 50 | 82.4 | 24 | 74 | 32.2 | 212.2 | 222.1 | 212.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-029191
TR_B (available) | 48-007764
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 82.4
TR_B Baseline Loading% | 24
Total Scenarios Evaluated | 16
Feasible Scenarios | 12
--- Optimal Solution ---
Switch Parent Node | 31
Switch Child Node | 6
Tie Node (TR_A side) | 2
Tie Node (TR_B side) | 28
Tie Line Distance (m) | 67.6
Load Transferred (kW) | 4.14
TR_A Loading After (%) | 65.9
TR_B Loading After (%) | 40.7
Minimum Voltage (V) | 214.2