## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 11 | 12 | 2 | 25 | 58.7 | 20.95 | 50 | 82.4 | 28.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 12 | 9 | 2 | 25 | 58.7 | 20.76 | 50 | 82.4 | 28.5 | [5 empty] | NO | TR_B sim: not converged
1 | ** OPTIMAL ** | 9 | 16 | 2 | 25 | 58.7 | 3.1 | 50 | 82.4 | 28.5 | 70.1 | 32.2 | 211.4 | 214.5 | 211.4 | YES
2 | OK | 16 | 25 | 2 | 25 | 58.7 | 2.36 | 50 | 82.4 | 28.5 | 73 | 31.3 | 210.7 | 214.7 | 210.7 | YES
3 | OK | 25 | 41 | 2 | 25 | 58.7 | 2.1 | 50 | 82.4 | 28.5 | 74 | 31 | 210.4 | 214.8 | 210.4 | YES
4 | OK | 41 | 39 | 2 | 25 | 58.7 | 2.08 | 50 | 82.4 | 28.5 | 74.1 | 31 | 210.4 | 214.8 | 210.4 | YES
5 | OK | 39 | 37 | 2 | 25 | 58.7 | 2.08 | 50 | 82.4 | 28.5 | 74.1 | 31 | 210.4 | 214.8 | 210.4 | YES
6 | OK | 37 | 18 | 2 | 25 | 58.7 | 2.08 | 50 | 82.4 | 28.5 | 74.1 | 31 | 210.4 | 214.8 | 210.4 | YES
7 | OK | 18 | 17 | 2 | 25 | 58.7 | 2.06 | 50 | 82.4 | 28.5 | 74.2 | 30.9 | 210.4 | 214.8 | 210.4 | YES
8 | OK | 17 | 38 | 2 | 25 | 58.7 | 2.04 | 50 | 82.4 | 28.5 | 74.3 | 30.9 | 210.4 | 214.8 | 210.4 | YES
9 | OK | 38 | 20 | 2 | 25 | 58.7 | 2.04 | 50 | 82.4 | 28.5 | 74.3 | 30.9 | 210.4 | 214.8 | 210.4 | YES
10 | OK | 20 | 19 | 2 | 25 | 58.7 | 1.92 | 50 | 82.4 | 28.5 | 74.7 | 30.8 | 210.3 | 214.8 | 210.3 | YES
11 | OK | 19 | 21 | 2 | 25 | 58.7 | 1.83 | 50 | 82.4 | 28.5 | 75.1 | 30.7 | 210.2 | 214.8 | 210.2 | YES
| NG | 21 | 23 | 2 | 25 | 58.7 | 1.34 | 50 | 82.4 | 28.5 | 77 | 30.1 | 209.7 | 215 | 209.7 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 60-029560
TR_B (available) | 55-012468
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 82.4
TR_B Baseline Loading% | 28.5
Total Scenarios Evaluated | 14
Feasible Scenarios | 11
--- Optimal Solution ---
Switch Parent Node | 9
Switch Child Node | 16
Tie Node (TR_A side) | 2
Tie Node (TR_B side) | 25
Tie Line Distance (m) | 58.7
Load Transferred (kW) | 3.1
TR_A Loading After (%) | 70.1
TR_B Loading After (%) | 32.2
Minimum Voltage (V) | 211.4