## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 22 | 12 | 13 | 16 | 2.9 | 13.46 | 50 | 80.6 | 25.6 | 28 | 78.5 | 225.6 | 214.9 | 214.9 | YES
2 | OK | 12 | 11 | 13 | 16 | 2.9 | 13.31 | 50 | 80.6 | 25.6 | 28.6 | 77.9 | 225.5 | 214.9 | 214.9 | YES
3 | OK | 11 | 42 | 13 | 16 | 2.9 | 12.39 | 50 | 80.6 | 25.6 | 32.1 | 74.2 | 224.9 | 217 | 217 | YES
4 | OK | 42 | 21 | 13 | 16 | 2.9 | 12.39 | 50 | 80.6 | 25.6 | 32.1 | 74.2 | 224.9 | 217 | 217 | YES
5 | OK | 21 | 20 | 13 | 16 | 2.9 | 8.65 | 50 | 80.6 | 25.6 | 46.6 | 59.4 | 220.2 | 216.7 | 216.7 | YES
6 | OK | 20 | 41 | 13 | 16 | 2.9 | 8.65 | 50 | 80.6 | 25.6 | 46.6 | 59.4 | 220.2 | 216.7 | 216.7 | YES
7 | OK | 41 | 19 | 13 | 16 | 2.9 | 8.65 | 50 | 80.6 | 25.6 | 46.6 | 59.4 | 220.2 | 216.7 | 216.7 | YES
8 | OK | 19 | 18 | 13 | 16 | 2.9 | 8.44 | 50 | 80.6 | 25.6 | 47.4 | 58.6 | 220.2 | 217.1 | 217.1 | YES
9 | OK | 18 | 37 | 39 | 1 | 130.2 | 0.64 | 50 | 80.6 | 25.6 | 78.1 | 27.3 | 215.1 | 225.8 | 215.1 | YES
10 | OK | 18 | 17 | 13 | 16 | 2.9 | 7.76 | 50 | 80.6 | 25.6 | 50 | 55.8 | 220.3 | 218.5 | 218.5 | YES
11 | OK | 37 | 38 | 39 | 1 | 130.2 | 0.4 | 50 | 80.6 | 25.6 | 79 | 27.2 | 214.8 | 225.9 | 214.8 | YES
12 | OK | 17 | 16 | 13 | 16 | 2.9 | 7.7 | 50 | 80.6 | 25.6 | 50.2 | 55.6 | 220.3 | 218.6 | 218.6 | YES
13 | OK | 38 | 39 | 39 | 1 | 130.2 | 0.32 | 50 | 80.6 | 25.6 | 79.3 | 25.6 | 214.6 | 226.6 | 214.6 | YES
14 | OK | 16 | 15 | 13 | 16 | 2.9 | 7.09 | 50 | 80.6 | 25.6 | 52.6 | 53.2 | 220.3 | 219.5 | 219.5 | YES
15 | OK | 16 | 34 | 36 | 1 | 89.8 | 0.61 | 50 | 80.6 | 25.6 | 78.1 | 28 | 215.2 | 225.6 | 215.2 | YES
16 | ** OPTIMAL ** | 15 | 14 | 13 | 16 | 2.9 | 6.14 | 50 | 80.6 | 25.6 | 56.2 | 49.5 | 219.8 | 220 | 219.8 | YES
17 | OK | 34 | 36 | 36 | 1 | 89.8 | 0.61 | 50 | 80.6 | 25.6 | 78.1 | 25.8 | 215.2 | 226.5 | 215.2 | YES
18 | OK | 14 | 13 | 13 | 16 | 2.9 | 4.82 | 50 | 80.6 | 25.6 | 61.3 | 44.3 | 219.6 | 221.2 | 219.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-030612
TR_B (available) | 60-007811
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 80.6
TR_B Baseline Loading% | 25.6
Total Scenarios Evaluated | 18
Feasible Scenarios | 18
--- Optimal Solution ---
Switch Parent Node | 15
Switch Child Node | 14
Tie Node (TR_A side) | 13
Tie Node (TR_B side) | 16
Tie Line Distance (m) | 2.9
Load Transferred (kW) | 6.14
TR_A Loading After (%) | 56.2
TR_B Loading After (%) | 49.5
Minimum Voltage (V) | 219.8