## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 22 | 23 | 10 | 25 | 38.8 | 7.18 | 50 | 80.6 | 60 | 52.9 | 68.6 | 216.7 | 204 | 204 | NO
| NG | 23 | 43 | 10 | 25 | 38.8 | 6.59 | 50 | 80.6 | 60 | 55.2 | 66.9 | 216.3 | 207.4 | 207.4 | NO
| NG | 43 | 31 | 10 | 25 | 38.8 | 6.59 | 50 | 80.6 | 60 | 55.2 | 46.4 | 216.3 | 8 | 8 | NO
| NG | 31 | 25 | 10 | 25 | 38.8 | 6.44 | 50 | 80.6 | 60 | 55.8 | 66.5 | 216.2 | 208.2 | 208.2 | NO
| NG | 25 | 4 | 10 | 25 | 38.8 | 6.44 | 50 | 80.6 | 60 | 55.8 | 66.5 | 216.2 | 208.2 | 208.2 | NO
| NG | 4 | 3 | 10 | 25 | 38.8 | 4.19 | 50 | 80.6 | 60 | 64.4 | 66.5 | 216.2 | 208.2 | 208.2 | NO
1 | OK | 3 | 5 | 10 | 25 | 38.8 | 3.79 | 50 | 80.6 | 60 | 65.9 | 65.5 | 215.9 | 210.3 | 210.3 | YES
2 | OK | 5 | 6 | 10 | 25 | 38.8 | 3.48 | 50 | 80.6 | 60 | 67.1 | 64.6 | 215.6 | 211.8 | 211.8 | YES
3 | ** OPTIMAL ** | 6 | 7 | 10 | 25 | 38.8 | 0.98 | 50 | 80.6 | 60 | 76.8 | 62.5 | 215 | 214.8 | 214.8 | YES
4 | OK | 7 | 8 | 10 | 25 | 38.8 | 0.71 | 50 | 80.6 | 60 | 77.8 | 61.8 | 214.8 | 214.7 | 214.7 | YES
5 | OK | 8 | 9 | 10 | 25 | 38.8 | 0.71 | 50 | 80.6 | 60 | 77.8 | 61.8 | 214.8 | 214.7 | 214.7 | YES
| NG | 9 | 33 | 10 | 25 | 38.8 | 0.71 | 50 | 80.6 | 60 |  | 61.8 | 6 | 214.7 | 6 | NO
6 | OK | 33 | 24 | 10 | 25 | 38.8 | 0.71 | 50 | 80.6 | 60 | 77.8 | 61.8 | 214.8 | 214.7 | 214.7 | YES
7 | OK | 24 | 10 | 10 | 25 | 38.8 | 0.32 | 50 | 80.6 | 60 | 79.3 | 60.8 | 214.5 | 214.4 | 214.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-030612
TR_B (available) | 61-008789
TR_A Rated kVA | 30
TR_B Rated kVA | 50
TR_A Baseline Loading% | 80.6
TR_B Baseline Loading% | 60
Total Scenarios Evaluated | 14
Feasible Scenarios | 7
--- Optimal Solution ---
Switch Parent Node | 6
Switch Child Node | 7
Tie Node (TR_A side) | 10
Tie Node (TR_B side) | 25
Tie Line Distance (m) | 38.8
Load Transferred (kW) | 0.98
TR_A Loading After (%) | 76.8
TR_B Loading After (%) | 62.5
Minimum Voltage (V) | 214.8