## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 34 | 35 | 38 | 30 | 4.5 | 14.6 | 50 | 87.8 | 34 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 34 | 48 | 48 | 29 | 52.6 | 8.02 | 50 | 87.8 | 34 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 35 | 39 | 38 | 30 | 4.5 | 14.15 | 50 | 87.8 | 34 | 32.6 | 54.1 | 222.8 | 197.8 | 197.8 | NO
1 | OK | 48 | 40 | 40 | 29 | 59.2 | 7.33 | 50 | 87.8 | 34 | 59.6 | 36.6 | 216.9 | 221.6 | 216.9 | YES
| NG | 39 | 3 | 38 | 30 | 4.5 | 14.15 | 50 | 87.8 | 34 | 32.6 | 54.1 | 222.8 | 197.8 | 197.8 | NO
| NG | 40 | 63 | 56 | 24 | 81.5 | 6.24 | 50 | 87.8 | 34 | 63.7 | 49.9 | 216 | 204.2 | 204.2 | NO
2 | OK | 3 | 2 | 58 | 19 | 50.9 | 11.39 | 50 | 87.8 | 34 | 43.1 | 47.5 | 222.3 | 219.5 | 219.5 | YES
| NG | 63 | 54 | 56 | 24 | 81.5 | 5.89 | 50 | 87.8 | 34 | 65.1 | 48.9 | 216 | 205.5 | 205.5 | NO
3 | OK | 2 | 5 | 58 | 19 | 50.9 | 11.05 | 50 | 87.8 | 34 | 44.4 | 47.5 | 222 | 219.5 | 219.5 | YES
| NG | 54 | 53 | 56 | 24 | 81.5 | 5.89 | 50 | 87.8 | 34 | 65.1 | 48.9 | 216 | 205.5 | 205.5 | NO
4 | OK | 5 | 4 | 58 | 19 | 50.9 | 11.05 | 50 | 87.8 | 34 | 44.4 | 47.5 | 222 | 219.5 | 219.5 | YES
| NG | 53 | 55 | 56 | 24 | 81.5 | 5.16 | 50 | 87.8 | 34 | 67.9 | 47 | 216 | 208.2 | 208.2 | NO
5 | OK | 4 | 6 | 58 | 19 | 50.9 | 10.97 | 50 | 87.8 | 34 | 44.7 | 47.5 | 222 | 219.5 | 219.5 | YES
6 | OK | 55 | 67 | 56 | 24 | 81.5 | 4.41 | 50 | 87.8 | 34 | 70.7 | 45 | 216 | 210.8 | 210.8 | YES
7 | OK | 6 | 76 | 58 | 19 | 50.9 | 10.77 | 50 | 87.8 | 34 | 45.5 | 47.5 | 221.8 | 219.5 | 219.5 | YES
8 | OK | 67 | 41 | 56 | 24 | 81.5 | 4.41 | 50 | 87.8 | 34 | 70.7 | 45 | 216 | 210.8 | 210.8 | YES
9 | OK | 76 | 30 | 58 | 19 | 50.9 | 10.11 | 50 | 87.8 | 34 | 48 | 47.5 | 221.3 | 219.5 | 219.5 | YES
10 | OK | 30 | 29 | 58 | 19 | 50.9 | 8.87 | 50 | 87.8 | 34 | 52.8 | 44.6 | 221.3 | 220.1 | 220.1 | YES
11 | ** OPTIMAL ** | 29 | 8 | 58 | 19 | 50.9 | 8.19 | 50 | 87.8 | 34 | 55.4 | 43.8 | 221.1 | 220.3 | 220.3 | YES
12 | OK | 8 | 14 | 18 | 21 | 82.8 | 5.44 | 50 | 87.8 | 34 | 66.1 | 46.8 | 220.4 | 220.3 | 220.3 | YES
13 | OK | 14 | 13 | 18 | 21 | 82.8 | 5.44 | 50 | 87.8 | 34 | 66.1 | 46.8 | 220.4 | 220.3 | 220.3 | YES
14 | OK | 13 | 22 | 18 | 21 | 82.8 | 5.16 | 50 | 87.8 | 34 | 67.2 | 46.1 | 220.2 | 220.2 | 220.2 | YES
15 | OK | 22 | 18 | 18 | 21 | 82.8 | 4.7 | 50 | 87.8 | 34 | 69 | 45 | 219.9 | 220.1 | 219.9 | YES
16 | OK | 18 | 72 | 72 | 18 | 86 | 2.39 | 50 | 87.8 | 34 | 78.3 | 39.6 | 215.1 | 222.8 | 215.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-031433
TR_B (available) | 45-011680
TR_A Rated kVA | 30
TR_B Rated kVA | 50
TR_A Baseline Loading% | 87.8
TR_B Baseline Loading% | 34
Total Scenarios Evaluated | 24
Feasible Scenarios | 16
--- Optimal Solution ---
Switch Parent Node | 29
Switch Child Node | 8
Tie Node (TR_A side) | 58
Tie Node (TR_B side) | 19
Tie Line Distance (m) | 50.9
Load Transferred (kW) | 8.19
TR_A Loading After (%) | 55.4
TR_B Loading After (%) | 43.8
Minimum Voltage (V) | 220.3