## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 15 | 33 | 45 | 30 | 3.2 | 8.08 | 50 | 75.2 | 52.7 | 56.2 | 76.4 | 217.2 | 201.6 | 201.6 | NO
| NG | 33 | 32 | 45 | 30 | 3.2 | 6.35 | 50 | 75.2 | 52.7 | 60.2 | 68.6 | 217.2 | 209 | 209 | NO
| NG | 32 | 53 | 45 | 30 | 3.2 | 4.73 | 50 | 75.2 | 52.7 | 60.2 | 68.6 | 217.2 | 209 | 209 | NO
| NG | 53 | 52 | 45 | 30 | 3.2 | 3.81 | 50 | 75.2 | 52.7 | 66.1 | 68.6 | 217.2 | 209 | 209 | NO
| NG | 52 | 54 | 45 | 30 | 3.2 | 3.7 | 50 | 75.2 | 52.7 | 66.4 | 68.1 | 217.2 | 208.9 | 208.9 | NO
| NG | 54 | 13 | 45 | 30 | 3.2 | 3.64 | 50 | 75.2 | 52.7 | 66.5 | 67.9 | 217.2 | 209.1 | 209.1 | NO
| NG | 13 | 14 | 14 | 30 | 51 | 3.57 | 50 | 75.2 | 52.7 | 66.7 | 67.5 | 217.2 | 209.8 | 209.8 | NO
1 | ** OPTIMAL ** | 14 | 56 | 56 | 30 | 52.2 | 3.57 | 50 | 75.2 | 52.7 | 66.7 | 52.7 | 217.2 | 217.7 | 217.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-032861
TR_B (available) | 65-000219
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 75.2
TR_B Baseline Loading% | 52.7
Total Scenarios Evaluated | 8
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 14
Switch Child Node | 56
Tie Node (TR_A side) | 56
Tie Node (TR_B side) | 30
Tie Line Distance (m) | 52.2
Load Transferred (kW) | 3.57
TR_A Loading After (%) | 66.7
TR_B Loading After (%) | 52.7
Minimum Voltage (V) | 217.2