## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 0 | 1 | 26 | 11 | 45.1 | 9.12 | 50 | 82.4 | 44.6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 0 | 27 | 17 | 7 | 44.5 | 12.12 | 50 | 82.4 | 44.6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 1 | 26 | 26 | 11 | 45.1 | 6.56 | 50 | 82.4 | 44.6 | 57.1 | 52.3 | 214.3 | 214.1 | 214.1 | YES
2 | OK | 27 | 14 | 17 | 7 | 44.5 | 11.63 | 50 | 82.4 | 44.6 | 36.9 | 58.6 | 223 | 213.3 | 213.3 | YES
3 | OK | 26 | 25 | 25 | 10 | 45.4 | 6.2 | 50 | 82.4 | 44.6 | 58.5 | 51.9 | 214 | 213.7 | 213.7 | YES
4 | OK | 14 | 15 | 17 | 7 | 44.5 | 9.98 | 50 | 82.4 | 44.6 | 43.2 | 56.5 | 223 | 214.1 | 214.1 | YES
5 | OK | 25 | 24 | 24 | 38 | 46.3 | 4.39 | 50 | 82.4 | 44.6 | 65.5 | 49.8 | 212.9 | 213.5 | 212.9 | YES
6 | OK | 15 | 4 | 17 | 7 | 44.5 | 8.33 | 50 | 82.4 | 44.6 | 49.5 | 54.5 | 223 | 214.6 | 214.6 | YES
7 | OK | 24 | 13 | 13 | 39 | 48.1 | 2.82 | 50 | 82.4 | 44.6 | 71.5 | 47.9 | 212.1 | 213.8 | 212.1 | YES
8 | OK | 4 | 3 | 17 | 7 | 44.5 | 8.01 | 50 | 82.4 | 44.6 | 50.8 | 54.1 | 223 | 214.6 | 214.6 | YES
9 | OK | 13 | 12 | 11 | 54 | 48.2 | 1.43 | 50 | 82.4 | 44.6 | 76.9 | 46.3 | 211 | 213.4 | 211 | YES
10 | OK | 3 | 2 | 17 | 7 | 44.5 | 7.91 | 50 | 82.4 | 44.6 | 51.1 | 54 | 223 | 214.7 | 214.7 | YES
11 | OK | 12 | 11 | 11 | 54 | 48.2 | 1.43 | 50 | 82.4 | 44.6 | 76.9 | 46.2 | 211 | 213.4 | 211 | YES
12 | OK | 2 | 16 | 17 | 7 | 44.5 | 6.49 | 50 | 82.4 | 44.6 | 56.6 | 52.3 | 222.8 | 214.3 | 214.3 | YES
13 | OK | 16 | 6 | 6 | 52 | 61.9 | 6.49 | 50 | 82.4 | 44.6 | 56.6 | 52.3 | 222.8 | 214.7 | 214.7 | YES
14 | OK | 6 | 5 | 5 | 52 | 93 | 4.86 | 50 | 82.4 | 44.6 | 63.1 | 50.4 | 219.5 | 214.2 | 214.2 | YES
15 | ** OPTIMAL ** | 5 | 19 | 19 | 53 | 95.1 | 4.84 | 50 | 82.4 | 44.6 | 63.1 | 50.4 | 219.5 | 215.4 | 215.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-033714
TR_B (available) | 58-004407
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 82.4
TR_B Baseline Loading% | 44.6
Total Scenarios Evaluated | 17
Feasible Scenarios | 15
--- Optimal Solution ---
Switch Parent Node | 5
Switch Child Node | 19
Tie Node (TR_A side) | 19
Tie Node (TR_B side) | 53
Tie Line Distance (m) | 95.1
Load Transferred (kW) | 4.84
TR_A Loading After (%) | 63.1
TR_B Loading After (%) | 50.4
Minimum Voltage (V) | 215.4