## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | ** OPTIMAL ** | 5 | 6 | 13 | 0 | 43.8 | 14.86 | 50 | 92.4 | 24.8 | 32.7 | 33.4 | 221.3 | 219.2 | 219.2 | YES
2 | OK | 6 | 20 | 13 | 0 | 43.8 | 6.63 | 50 | 92.4 | 24.8 | 65.3 | 32 | 211 | 219.5 | 211 | YES
3 | OK | 20 | 19 | 13 | 0 | 43.8 | 6.17 | 50 | 92.4 | 24.8 | 67 | 30.2 | 211.1 | 220 | 211.1 | YES
| NG | 19 | 18 | 13 | 0 | 43.8 | 3.73 | 50 | 92.4 | 24.8 | 77 | 29.7 | 207.8 | 220.1 | 207.8 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 60-034137
TR_B (available) | 43-003657
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 92.4
TR_B Baseline Loading% | 24.8
Total Scenarios Evaluated | 4
Feasible Scenarios | 3
--- Optimal Solution ---
Switch Parent Node | 5
Switch Child Node | 6
Tie Node (TR_A side) | 13
Tie Node (TR_B side) | 0
Tie Line Distance (m) | 43.8
Load Transferred (kW) | 14.86
TR_A Loading After (%) | 32.7
TR_B Loading After (%) | 33.4
Minimum Voltage (V) | 219.2