## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 9 | 8 | 44 | 22 | 3.7 | 15.09 | 50 | 83.3 | 24 | 24.3 | 89.4 | 223.1 | 186.4 | 186.4 | NO
| NG | 8 | 4 | 44 | 22 | 3.7 | 13.55 | 50 | 83.3 | 24 | 28.2 | 81.7 | 222.4 | 191.2 | 191.2 | NO
| NG | 4 | 5 | 44 | 22 | 3.7 | 12.49 | 50 | 83.3 | 24 | 34.2 | 76.6 | 221.2 | 194.4 | 194.4 | NO
| NG | 5 | 32 | 38 | 26 | 60.3 | 6.7 | 50 | 83.3 | 24 | 56.6 | 51.2 | 216.6 | 209 | 209 | NO
1 | OK | 5 | 34 | 44 | 22 | 3.7 | 5.79 | 50 | 83.3 | 24 | 60.3 | 47 | 215.2 | 213.8 | 213.8 | YES
| NG | 32 | 33 | 38 | 26 | 60.3 | 6.7 | 50 | 83.3 | 24 | 56.6 | 51.2 | 216.6 | 209 | 209 | NO
2 | ** OPTIMAL ** | 34 | 10 | 44 | 22 | 3.7 | 5.79 | 50 | 83.3 | 24 | 60.3 | 39.7 | 215.2 | 217.9 | 215.2 | YES
| NG | 33 | 36 | 38 | 26 | 60.3 | 6.7 | 50 | 83.3 | 24 | 56.6 | 51.2 | 216.6 | 209 | 209 | NO
3 | OK | 10 | 11 | 44 | 22 | 3.7 | 4.01 | 50 | 83.3 | 24 | 67.3 | 39.7 | 213.1 | 217.9 | 213.1 | YES
4 | OK | 36 | 37 | 38 | 26 | 60.3 | 1.25 | 50 | 83.3 | 24 | 78.2 | 28.9 | 210.1 | 222.7 | 210.1 | YES
5 | OK | 11 | 27 | 44 | 22 | 3.7 | 1.75 | 50 | 83.3 | 24 | 76.2 | 30.8 | 210.4 | 222.6 | 210.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-034960
TR_B (available) | 50-006701
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 83.3
TR_B Baseline Loading% | 24
Total Scenarios Evaluated | 11
Feasible Scenarios | 5
--- Optimal Solution ---
Switch Parent Node | 34
Switch Child Node | 10
Tie Node (TR_A side) | 44
Tie Node (TR_B side) | 22
Tie Line Distance (m) | 3.7
Load Transferred (kW) | 5.79
TR_A Loading After (%) | 60.3
TR_B Loading After (%) | 39.7
Minimum Voltage (V) | 215.2