## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 17 | 22 | 25 | 24 | 1.6 | 1.37 | 50 | 82.9 | 73.1 | 77.5 | 73.3 | 215.1 | 215.3 | 215.1 | YES
2 | OK | 17 | 28 | 28 | 22 | 100.5 | 1.24 | 50 | 82.9 | 73.1 | 78.1 | 77.8 | 216.3 | 214.2 | 214.2 | YES
| NG | 14 | 15 | 20 | 22 | 4 | 1.91 | 50 | 82.9 | 73.1 | 75.5 | 80.4 | 216.1 | 214.6 | 214.6 | NO
3 | OK | 22 | 16 | 16 | 18 | 71.6 | 1.37 | 50 | 82.9 | 73.1 | 77.5 | 73.3 | 215.1 | 215.2 | 215.1 | YES
4 | OK | 15 | 12 | 20 | 22 | 4 | 1.56 | 50 | 82.9 | 73.1 | 76.8 | 79.1 | 216.1 | 214.6 | 214.6 | YES
5 | ** OPTIMAL ** | 16 | 4 | 4 | 18 | 72 | 1.37 | 50 | 82.9 | 73.1 | 77.5 | 73.3 | 215.1 | 215.2 | 215.1 | YES
6 | OK | 12 | 13 | 20 | 22 | 4 | 1.56 | 50 | 82.9 | 73.1 | 76.8 | 75.3 | 216.1 | 214.8 | 214.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-034965
TR_B (available) | 60-034964
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 82.9
TR_B Baseline Loading% | 73.1
Total Scenarios Evaluated | 7
Feasible Scenarios | 6
--- Optimal Solution ---
Switch Parent Node | 16
Switch Child Node | 4
Tie Node (TR_A side) | 4
Tie Node (TR_B side) | 18
Tie Line Distance (m) | 72
Load Transferred (kW) | 1.37
TR_A Loading After (%) | 77.5
TR_B Loading After (%) | 73.3
Minimum Voltage (V) | 215.1