## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 17 | 14 | 11 | 14 | 29 | 18.79 | 50 | 82.9 | 4.9 | 4.9 | 44.9 | 230 | 206.3 | 206.3 | NO
1 | OK | 17 | 22 | 26 | 12 | 42.1 | 1.37 | 50 | 82.9 | 4.9 | 77.5 | 5.1 | 215.1 | 228.8 | 215.1 | YES
2 | OK | 14 | 5 | 11 | 14 | 29 | 10.03 | 50 | 82.9 | 4.9 | 43.8 | 33.4 | 221.3 | 214.6 | 214.6 | YES
3 | OK | 5 | 6 | 11 | 14 | 29 | 8.74 | 50 | 82.9 | 4.9 | 48.7 | 28.9 | 221.2 | 217.4 | 217.4 | YES
4 | OK | 6 | 7 | 11 | 14 | 29 | 5.94 | 50 | 82.9 | 4.9 | 59.5 | 22.1 | 219.5 | 220.8 | 219.5 | YES
5 | ** OPTIMAL ** | 7 | 8 | 11 | 14 | 29 | 3.46 | 50 | 82.9 | 4.9 | 69.2 | 15 | 219.5 | 224 | 219.5 | YES
6 | OK | 8 | 9 | 11 | 14 | 29 | 2.59 | 50 | 82.9 | 4.9 | 72.6 | 15 | 218.7 | 224 | 218.7 | YES
7 | OK | 9 | 10 | 11 | 14 | 29 | 2.59 | 50 | 82.9 | 4.9 | 72.6 | 15 | 218.7 | 224 | 218.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-034965
TR_B (available) | 63-029109
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 82.9
TR_B Baseline Loading% | 4.9
Total Scenarios Evaluated | 8
Feasible Scenarios | 7
--- Optimal Solution ---
Switch Parent Node | 7
Switch Child Node | 8
Tie Node (TR_A side) | 11
Tie Node (TR_B side) | 14
Tie Line Distance (m) | 29
Load Transferred (kW) | 3.46
TR_A Loading After (%) | 69.2
TR_B Loading After (%) | 15
Minimum Voltage (V) | 219.5