## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 17 | 22 | 26 | 4 | 2.4 | 1.37 | 50 | 82.9 | 25 | 77.5 | 25.2 | 215.1 | 227.7 | 215.1 | YES
2 | OK | 14 | 5 | 10 | 8 | 101.3 | 10.03 | 50 | 82.9 | 25 | 43.8 | 53 | 221.3 | 217.5 | 217.5 | YES
3 | OK | 14 | 15 | 20 | 6 | 65.5 | 1.91 | 50 | 82.9 | 25 | 75.5 | 32.4 | 216.1 | 225.9 | 216.1 | YES
4 | OK | 14 | 1 | 1 | 6 | 127.3 | 6.85 | 50 | 82.9 | 25 | 51.1 | 52.1 | 216.7 | 215.9 | 215.9 | YES
5 | ** OPTIMAL ** | 5 | 6 | 10 | 8 | 101.3 | 8.74 | 50 | 82.9 | 25 | 48.7 | 48.6 | 221.2 | 219.6 | 219.6 | YES
6 | OK | 15 | 12 | 20 | 6 | 65.5 | 1.56 | 50 | 82.9 | 25 | 76.8 | 31 | 216.1 | 226.4 | 216.1 | YES
7 | OK | 1 | 0 | 0 | 6 | 148 | 6.57 | 50 | 82.9 | 25 | 52.2 | 50.9 | 216.7 | 216.9 | 216.7 | YES
8 | OK | 6 | 7 | 10 | 8 | 101.3 | 5.94 | 50 | 82.9 | 25 | 59.5 | 42 | 219.5 | 222 | 219.5 | YES
9 | OK | 12 | 13 | 20 | 6 | 65.5 | 1.56 | 50 | 82.9 | 25 | 76.8 | 27.3 | 216.1 | 226.8 | 216.1 | YES
10 | OK | 7 | 8 | 10 | 8 | 101.3 | 3.46 | 50 | 82.9 | 25 | 69.2 | 35 | 219.5 | 224.2 | 219.5 | YES
11 | OK | 8 | 9 | 10 | 8 | 101.3 | 2.59 | 50 | 82.9 | 25 | 72.6 | 35 | 218.7 | 224.2 | 218.7 | YES
12 | OK | 9 | 10 | 10 | 8 | 101.3 | 2.59 | 50 | 82.9 | 25 | 72.6 | 35 | 218.7 | 224.2 | 218.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-034965
TR_B (available) | 66-011707
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 82.9
TR_B Baseline Loading% | 25
Total Scenarios Evaluated | 12
Feasible Scenarios | 12
--- Optimal Solution ---
Switch Parent Node | 5
Switch Child Node | 6
Tie Node (TR_A side) | 10
Tie Node (TR_B side) | 8
Tie Line Distance (m) | 101.3
Load Transferred (kW) | 8.74
TR_A Loading After (%) | 48.7
TR_B Loading After (%) | 48.6
Minimum Voltage (V) | 219.6