## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 17 | 14 | 14 | 17 | 44.1 | 18.79 | 50 | 82.9 | 6.3 | 4.9 | 44.9 | 230 | 212.4 | 212.4 | YES
2 | OK | 17 | 22 | 22 | 17 | 45.5 | 1.37 | 50 | 82.9 | 6.3 | 77.5 | 6.5 | 215.1 | 229.4 | 215.1 | YES
3 | OK | 17 | 28 | 28 | 17 | 0.9 | 1.24 | 50 | 82.9 | 6.3 | 78.1 | 11 | 216.3 | 228.5 | 216.3 | YES
4 | OK | 14 | 5 | 5 | 17 | 70.2 | 10.03 | 50 | 82.9 | 6.3 | 43.8 | 34.3 | 221.3 | 216.7 | 216.7 | YES
5 | OK | 14 | 15 | 15 | 17 | 53 | 1.91 | 50 | 82.9 | 6.3 | 75.5 | 9.6 | 216.1 | 228.7 | 216.1 | YES
6 | OK | 14 | 1 | 1 | 17 | 53.1 | 6.85 | 50 | 82.9 | 6.3 | 51.1 | 13.1 | 216.7 | 227.4 | 216.7 | YES
7 | OK | 22 | 16 | 3 | 17 | 146.3 | 1.37 | 50 | 82.9 | 6.3 | 77.5 | 6.5 | 215.1 | 229.4 | 215.1 | YES
8 | ** OPTIMAL ** | 5 | 6 | 8 | 9 | 102.2 | 8.74 | 50 | 82.9 | 6.3 | 48.7 | 6.3 | 221.2 | 229.4 | 221.2 | YES
9 | OK | 15 | 12 | 12 | 17 | 78.5 | 1.56 | 50 | 82.9 | 6.3 | 76.8 | 9.4 | 216.1 | 228.7 | 216.1 | YES
10 | OK | 1 | 0 | 0 | 17 | 80.2 | 6.57 | 50 | 82.9 | 6.3 | 52.2 | 13.1 | 216.7 | 227.5 | 216.7 | YES
11 | OK | 16 | 4 | 3 | 17 | 146.3 | 1.37 | 50 | 82.9 | 6.3 | 77.5 | 6.5 | 215.1 | 229.4 | 215.1 | YES
12 | OK | 6 | 7 | 8 | 9 | 102.2 | 5.94 | 50 | 82.9 | 6.3 | 59.5 | 6.3 | 219.5 | 229.4 | 219.5 | YES
13 | OK | 12 | 13 | 13 | 17 | 93.9 | 1.56 | 50 | 82.9 | 6.3 | 76.8 | 8.5 | 216.1 | 229 | 216.1 | YES
14 | OK | 0 | 2 | 2 | 17 | 110.7 | 3.46 | 50 | 82.9 | 6.3 | 64.2 | 6.3 | 215 | 229.4 | 215 | YES
15 | OK | 7 | 8 | 8 | 9 | 102.2 | 3.46 | 50 | 82.9 | 6.3 | 69.2 | 6.3 | 219.5 | 229.4 | 219.5 | YES
16 | OK | 8 | 9 | 11 | 13 | 104.9 | 2.59 | 50 | 82.9 | 6.3 | 72.6 | 6.3 | 218.7 | 229.4 | 218.7 | YES
17 | OK | 9 | 10 | 11 | 13 | 104.9 | 2.59 | 50 | 82.9 | 6.3 | 72.6 | 6.3 | 218.7 | 229.4 | 218.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-034965
TR_B (available) | 66-018997
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 82.9
TR_B Baseline Loading% | 6.3
Total Scenarios Evaluated | 17
Feasible Scenarios | 17
--- Optimal Solution ---
Switch Parent Node | 5
Switch Child Node | 6
Tie Node (TR_A side) | 8
Tie Node (TR_B side) | 9
Tie Line Distance (m) | 102.2
Load Transferred (kW) | 8.74
TR_A Loading After (%) | 48.7
TR_B Loading After (%) | 6.3
Minimum Voltage (V) | 221.2