## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 5 | 6 | 20 | 15 | 2.2 | 14.27 | 50 | 83.9 | 28.9 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 6 | 21 | 20 | 15 | 2.2 | 13.53 | 50 | 83.9 | 28.9 | 25.1 | 84.7 | 225.9 | 199.6 | 199.6 | NO
| NG | 21 | 27 | 20 | 15 | 2.2 | 13.4 | 50 | 83.9 | 28.9 | 28.4 | 84.2 | 225.5 | 199.6 | 199.6 | NO
| NG | 27 | 3 | 20 | 15 | 2.2 | 13.33 | 50 | 83.9 | 28.9 | 28.7 | 83.9 | 225.5 | 199.8 | 199.8 | NO
| NG | 3 | 2 | 20 | 15 | 2.2 | 13.33 | 50 | 83.9 | 28.9 | 28.7 | 83.9 | 225.5 | 199.8 | 199.8 | NO
| NG | 2 | 0 | 20 | 15 | 2.2 | 11.57 | 50 | 83.9 | 28.9 | 35.4 | 77.2 | 224.2 | 199.3 | 199.3 | NO
| NG | 0 | 1 | 20 | 15 | 2.2 | 11.03 | 50 | 83.9 | 28.9 | 37.5 | 75.1 | 223.8 | 199.1 | 199.1 | NO
| NG | 1 | 17 | 17 | 15 | 99.4 | 9.31 | 50 | 83.9 | 28.9 | 44.1 | 67.6 | 223.9 | 203.3 | 203.3 | NO
1 | OK | 17 | 19 | 19 | 13 | 110.2 | 9.31 | 50 | 83.9 | 28.9 | 44.1 | 30.2 | 223.9 | 220.3 | 220.3 | YES
2 | ** OPTIMAL ** | 19 | 14 | 14 | 13 | 112.1 | 7.75 | 50 | 83.9 | 28.9 | 50.3 | 30.2 | 221.3 | 220.3 | 220.3 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-034997
TR_B (available) | 57-951086
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 83.9
TR_B Baseline Loading% | 28.9
Total Scenarios Evaluated | 10
Feasible Scenarios | 2
--- Optimal Solution ---
Switch Parent Node | 19
Switch Child Node | 14
Tie Node (TR_A side) | 14
Tie Node (TR_B side) | 13
Tie Line Distance (m) | 112.1
Load Transferred (kW) | 7.75
TR_A Loading After (%) | 50.3
TR_B Loading After (%) | 30.2
Minimum Voltage (V) | 220.3