## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 4 | 5 | 13 | 43 | 240.1 | 33.29 | 50 | 79.4 | 14.4 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 4 | 42 | 29 | 3 | 2.7 | 34.17 | 50 | 79.4 | 14.4 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 5 | 6 | 13 | 43 | 240.1 | 21.59 | 50 | 79.4 | 14.4 | 54.4 | 23.3 | 208.9 | 205.5 | 205.5 | NO
| NG | 42 | 41 | 29 | 3 | 2.7 | 33.42 | 50 | 79.4 | 14.4 | [5 empty] | NO | TR_A sim: loading 3153% (degenerate)
| NG | 6 | 7 | 13 | 43 | 240.1 | 20.08 | 50 | 79.4 | 14.4 | 56.1 | 22.4 | 208.9 | 207.3 | 207.3 | NO
| NG | 41 | 37 | 29 | 3 | 2.7 | 31.27 | 50 | 79.4 | 14.4 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 14.4% (degenerate)
| NG | 7 | 9 | 13 | 43 | 240.1 | 19.17 | 50 | 79.4 | 14.4 | 56.6 | 22.4 | 208.8 | 207.3 | 207.3 | NO
| NG | 37 | 36 | 29 | 3 | 2.7 | 31.27 | 50 | 79.4 | 14.4 | 41.7 | 155 | 222.3 | 11.3 | 11.3 | NO
| NG | 9 | 8 | 13 | 43 | 240.1 | 17.3 | 50 | 79.4 | 14.4 | 59.3 | 21.2 | 208.7 | 209.7 | 208.7 | NO
| NG | 36 | 33 | 3 | 30 | 262.6 | 3.83 | 50 | 79.4 | 14.4 | 74.9 | 15.6 | 208.7 | 220.6 | 208.7 | NO
1 | OK | 36 | 62 | 29 | 3 | 2.7 | 27.44 | 50 | 79.4 | 14.4 | 46.1 | 46.6 | 222.1 | 218.9 | 218.9 | YES
| NG | 8 | 11 | 13 | 43 | 240.1 | 15.3 | 50 | 79.4 | 14.4 | 61.6 | 20.2 | 208.7 | 211.8 | 208.7 | NO
| NG | 33 | 34 | 3 | 30 | 262.6 | 3.69 | 50 | 79.4 | 14.4 | 75.1 | 15.6 | 208.7 | 220.6 | 208.7 | NO
2 | OK | 62 | 63 | 29 | 3 | 2.7 | 27.44 | 50 | 79.4 | 14.4 | 46.1 | 46.6 | 222.1 | 218.9 | 218.9 | YES
| NG | 11 | 10 | 13 | 43 | 240.1 | 5.35 | 50 | 79.4 | 14.4 | 73.2 | 16.3 | 208.2 | 219.6 | 208.2 | NO
| NG | 11 | 35 | 16 | 32 | 241.3 | 9.95 | 50 | 79.4 | 14.4 | 67.8 | 18.2 | 208.3 | 211.5 | 208.3 | NO
| NG | 34 | 38 | 3 | 30 | 262.6 | 2.58 | 50 | 79.4 | 14.4 | 76.4 | 15.6 | 208.7 | 220.6 | 208.7 | NO
3 | OK | 63 | 61 | 29 | 3 | 2.7 | 25.85 | 50 | 79.4 | 14.4 | 46.1 | 44.8 | 222.1 | 218.7 | 218.7 | YES
| NG | 10 | 12 | 13 | 43 | 240.1 | 4.02 | 50 | 79.4 | 14.4 | 74.7 | 16.3 | 208 | 219.6 | 208 | NO
| NG | 35 | 14 | 16 | 32 | 241.3 | 3.23 | 50 | 79.4 | 14.4 | 75.6 | 15.7 | 207.9 | 218.9 | 207.9 | NO
| NG | 35 | 18 | 18 | 31 | 282.8 | 6.6 | 50 | 79.4 | 14.4 | 71.5 | 16.8 | 208.1 | 216.7 | 208.1 | NO
| NG | 38 | 3 | 3 | 30 | 262.6 | 1.6 | 50 | 79.4 | 14.4 | 77.5 | 14.4 | 208.8 | 221.8 | 208.8 | NO
4 | OK | 61 | 45 | 29 | 3 | 2.7 | 25.85 | 50 | 79.4 | 14.4 | 48 | 44.8 | 222.1 | 218.7 | 218.7 | YES
| NG | 12 | 13 | 13 | 43 | 240.1 | 2.7 | 50 | 79.4 | 14.4 | 76.3 | 16.3 | 207.8 | 219.6 | 207.8 | NO
| NG | 14 | 15 | 16 | 32 | 241.3 | 2.05 | 50 | 79.4 | 14.4 | 77 | 14.6 | 207.9 | 221.4 | 207.9 | NO
| NG | 18 | 17 | 17 | 32 | 292.3 | 6.6 | 50 | 79.4 | 14.4 | 71.7 | 16.8 | 208.1 | 215.4 | 208.1 | NO
5 | OK | 45 | 44 | 29 | 3 | 2.7 | 24.37 | 50 | 79.4 | 14.4 | 49.7 | 43 | 222.1 | 219.9 | 219.9 | YES
| NG | 15 | 40 | 16 | 32 | 241.3 | 1.58 | 50 | 79.4 | 14.4 | 77.3 | 14.4 | 207.9 | 221.8 | 207.9 | NO
| NG | 17 | 46 | 19 | 42 | 295 | 5.78 | 50 | 79.4 | 14.4 | 72.6 | 16.6 | 208.1 | 214 | 208.1 | NO
6 | OK | 44 | 43 | 29 | 3 | 2.7 | 24.37 | 50 | 79.4 | 14.4 | 49.7 | 42.8 | 222.1 | 220.1 | 220.1 | YES
| NG | 40 | 16 | 16 | 32 | 241.3 | 1.35 | 50 | 79.4 | 14.4 | 77.6 | 14.4 | 207.9 | 221.8 | 207.9 | NO
| NG | 46 | 19 | 19 | 42 | 295 | 5.4 | 50 | 79.4 | 14.4 | 73.1 | 16.6 | 208.1 | 214 | 208.1 | NO
| NG | 43 | 30 | 29 | 3 | 2.7 | 3.38 | 50 | 79.4 | 14.4 | 75.1 | 18.3 | 209.8 | 221.8 | 209.8 | NO
7 | OK | 43 | 52 | 52 | 3 | 71.4 | 20.79 | 50 | 79.4 | 14.4 | 53.8 | 38.8 | 221.6 | 221.1 | 221.1 | YES
| NG | 30 | 29 | 29 | 3 | 2.7 | 0.71 | 50 | 79.4 | 14.4 | 78.5 | 15.2 | 208.9 | 221.8 | 208.9 | NO
8 | ** OPTIMAL ** | 52 | 53 | 53 | 3 | 75.5 | 20.79 | 50 | 79.4 | 14.4 | 53.8 | 38.7 | 221.6 | 221.3 | 221.3 | YES
9 | OK | 53 | 47 | 47 | 3 | 79 | 13.39 | 50 | 79.4 | 14.4 | 53.8 | 30 | 221.6 | 221.3 | 221.3 | YES
10 | OK | 47 | 48 | 48 | 3 | 92.7 | 13.39 | 50 | 79.4 | 14.4 | 63 | 30 | 211.1 | 221.3 | 211.1 | YES
11 | OK | 48 | 51 | 51 | 3 | 104.8 | 5.99 | 50 | 79.4 | 14.4 | 72 | 21.3 | 212.1 | 221.3 | 212.1 | YES
| NG | 51 | 49 | 49 | 3 | 109.6 | 2.34 | 50 | 79.4 | 14.4 | 75.5 | 17.1 | 208.5 | 221.7 | 208.5 | NO
12 | OK | 51 | 59 | 59 | 3 | 145.3 | 2.78 | 50 | 79.4 | 14.4 | 75.9 | 17.6 | 211.4 | 221.6 | 211.4 | YES
| NG | 49 | 50 | 50 | 3 | 128.7 | 2.34 | 50 | 79.4 | 14.4 | 76.5 | 17.1 | 208.8 | 221.7 | 208.8 | NO
| NG | 59 | 60 | 60 | 3 | 169.1 | 0.65 | 50 | 79.4 | 14.4 | 78.7 | 15.2 | 207.6 | 221.7 | 207.6 | NO
| NG | 50 | 58 | 58 | 3 | 158.6 | 0.85 | 50 | 79.4 | 14.4 | 78.4 | 15.4 | 208.3 | 221.7 | 208.3 | NO
| NG | 60 | 64 | 64 | 3 | 175 | 0.05 | 50 | 79.4 | 14.4 | 0 | 14.5 | 19.1 | 221.8 | 19.1 | NO
| NG | 58 | 54 | 54 | 3 | 195.4 | 0.53 | 50 | 79.4 | 14.4 | 78.8 | 15 | 207.6 | 221.7 | 207.6 | NO
| NG | 64 | 65 | 65 | 3 | 185 | 0.05 | 50 | 79.4 | 14.4 | 79.4 | 14.5 | 207.9 | 221.8 | 207.9 | NO
| NG | 54 | 55 | 55 | 3 | 197.8 | 0.53 | 50 | 79.4 | 14.4 | 78.8 | 14.4 | 207.6 | 221.8 | 207.6 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 60-036623
TR_B (available) | 67-021279
TR_A Rated kVA | 100
TR_B Rated kVA | 100
TR_A Baseline Loading% | 79.4
TR_B Baseline Loading% | 14.4
Total Scenarios Evaluated | 48
Feasible Scenarios | 12
--- Optimal Solution ---
Switch Parent Node | 52
Switch Child Node | 53
Tie Node (TR_A side) | 53
Tie Node (TR_B side) | 3
Tie Line Distance (m) | 75.5
Load Transferred (kW) | 20.79
TR_A Loading After (%) | 53.8
TR_B Loading After (%) | 38.7
Minimum Voltage (V) | 221.3