## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 19 | 20 | 41 | 13 | 41.6 | 5.46 | 50 | 80.2 | 53.1 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 20 | 21 | 41 | 13 | 41.6 | 4.8 | 50 | 80.2 | 53.1 | 61.8 | 72.7 | 219 | 212.7 | 212.7 | YES
2 | OK | 21 | 22 | 41 | 13 | 41.6 | 3.72 | 50 | 80.2 | 53.1 | 65.9 | 68.2 | 218.2 | 215.5 | 215.5 | YES
3 | OK | 4 | 5 | 5 | 6 | 19 | 5.04 | 50 | 80.2 | 53.1 | 60.6 | 73.1 | 218.3 | 215.3 | 215.3 | YES
4 | OK | 22 | 23 | 41 | 13 | 41.6 | 3.05 | 50 | 80.2 | 53.1 | 68.4 | 65.4 | 218.2 | 215.9 | 215.9 | YES
5 | OK | 5 | 12 | 12 | 6 | 52.6 | 5.03 | 50 | 80.2 | 53.1 | 60.6 | 73 | 218.3 | 215.4 | 215.4 | YES
6 | OK | 23 | 24 | 41 | 13 | 41.6 | 2.88 | 50 | 80.2 | 53.1 | 69.1 | 64.8 | 218.1 | 216.4 | 216.4 | YES
7 | OK | 23 | 38 | 39 | 11 | 51.1 | 0.17 | 50 | 80.2 | 53.1 | 79.5 | 53.8 | 217.2 | 219.7 | 217.2 | YES
8 | OK | 12 | 13 | 13 | 6 | 79.5 | 4.7 | 50 | 80.2 | 53.1 | 61.9 | 71.7 | 218.3 | 215.9 | 215.9 | YES
9 | OK | 24 | 8 | 41 | 13 | 41.6 | 2.49 | 50 | 80.2 | 53.1 | 70.6 | 63.2 | 218 | 217 | 217 | YES
10 | OK | 13 | 44 | 49 | 3 | 113 | 4.43 | 50 | 80.2 | 53.1 | 62.9 | 66.4 | 218.1 | 217.7 | 217.7 | YES
11 | OK | 3 | 2 | 2 | 7 | 89.3 | 6.37 | 50 | 80.2 | 53.1 | 55.3 | 78.5 | 220.3 | 212.5 | 212.5 | YES
12 | OK | 3 | 30 | 30 | 7 | 101.6 | 1.74 | 50 | 80.2 | 53.1 | 73.4 | 59.9 | 217.9 | 219.3 | 217.9 | YES
13 | OK | 8 | 9 | 41 | 13 | 41.6 | 1.59 | 50 | 80.2 | 53.1 | 74 | 59.5 | 217.3 | 217.8 | 217.3 | YES
14 | OK | 8 | 25 | 25 | 13 | 88.6 | 0.9 | 50 | 80.2 | 53.1 | 76.7 | 56.7 | 217.8 | 217.5 | 217.5 | YES
15 | OK | 44 | 15 | 49 | 3 | 113 | 4.43 | 50 | 80.2 | 53.1 | 62.9 | 66.4 | 218.1 | 217.7 | 217.7 | YES
16 | OK | 2 | 31 | 31 | 9 | 102.6 | 5.71 | 50 | 80.2 | 53.1 | 57.8 | 76.3 | 220.3 | 210.4 | 210.4 | YES
17 | OK | 30 | 28 | 28 | 7 | 118.1 | 1.42 | 50 | 80.2 | 53.1 | 74.6 | 58.7 | 217.5 | 219.8 | 217.5 | YES
18 | OK | 9 | 40 | 41 | 13 | 41.6 | 0.68 | 50 | 80.2 | 53.1 | 77.5 | 55.8 | 217.3 | 219.6 | 217.3 | YES
19 | OK | 25 | 26 | 26 | 13 | 109.7 | 0.37 | 50 | 80.2 | 53.1 | 78.7 | 54.6 | 217.4 | 219 | 217.4 | YES
20 | OK | 15 | 14 | 49 | 3 | 113 | 3.67 | 50 | 80.2 | 53.1 | 65.8 | 63.4 | 218.1 | 218.5 | 218.1 | YES
21 | OK | 31 | 32 | 32 | 11 | 110.5 | 4.77 | 50 | 80.2 | 53.1 | 61.4 | 72.7 | 220.1 | 210.5 | 210.5 | YES
| NG | 28 | 27 | 27 | 7 | 121.6 | 1.42 | 50 | 80.2 | 53.1 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 53.1% (degenerate)
22 | OK | 40 | 41 | 41 | 13 | 41.6 | 0.43 | 50 | 80.2 | 53.1 | 78.5 | 54.8 | 217.1 | 220.2 | 217.1 | YES
23 | OK | 26 | 7 | 7 | 13 | 132.2 | 0.28 | 50 | 80.2 | 53.1 | 79.1 | 54.2 | 217.3 | 219.3 | 217.3 | YES
24 | ** OPTIMAL ** | 14 | 16 | 49 | 3 | 113 | 3.19 | 50 | 80.2 | 53.1 | 67.7 | 61.5 | 218.1 | 219.1 | 218.1 | YES
25 | OK | 32 | 34 | 34 | 12 | 128.9 | 4.43 | 50 | 80.2 | 53.1 | 62.8 | 71.3 | 220.2 | 210.8 | 210.8 | YES
26 | OK | 16 | 43 | 49 | 3 | 113 | 2.8 | 50 | 80.2 | 53.1 | 69.2 | 61.1 | 217.8 | 219.2 | 217.8 | YES
27 | OK | 34 | 33 | 33 | 13 | 169.2 | 4.07 | 50 | 80.2 | 53.1 | 64.2 | 69.8 | 220.2 | 212 | 212 | YES
28 | OK | 43 | 47 | 49 | 3 | 113 | 1.84 | 50 | 80.2 | 53.1 | 72.9 | 60.3 | 217.1 | 219.4 | 217.1 | YES
29 | OK | 47 | 53 | 49 | 3 | 113 | 1.55 | 50 | 80.2 | 53.1 | 74 | 59.1 | 217.1 | 219.7 | 217.1 | YES
30 | OK | 53 | 51 | 49 | 3 | 113 | 1.07 | 50 | 80.2 | 53.1 | 75.9 | 57.3 | 217.1 | 220.2 | 217.1 | YES
31 | OK | 51 | 50 | 49 | 3 | 113 | 1.05 | 50 | 80.2 | 53.1 | 76 | 57.2 | 217.1 | 220.2 | 217.1 | YES
32 | OK | 50 | 49 | 49 | 3 | 113 | 0.06 | 50 | 80.2 | 53.1 | 79.9 | 53.3 | 217.1 | 220.1 | 217.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-039064
TR_B (available) | 45-016430
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 80.2
TR_B Baseline Loading% | 53.1
Total Scenarios Evaluated | 34
Feasible Scenarios | 32
--- Optimal Solution ---
Switch Parent Node | 14
Switch Child Node | 16
Tie Node (TR_A side) | 49
Tie Node (TR_B side) | 3
Tie Line Distance (m) | 113
Load Transferred (kW) | 3.19
TR_A Loading After (%) | 67.7
TR_B Loading After (%) | 61.5
Minimum Voltage (V) | 218.1