## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 6 | 5 | 1 | 48 | 68.3 | 9.96 | 50 | 100.4 | 55 | 61.7 | 62.9 | 218.9 | 204.9 | 204.9 | NO
| NG | 6 | 35 | 28 | 42 | 28.4 | 16.05 | 50 | 100.4 | 55 | 38.7 | 68 | 217.1 | 203.4 | 203.4 | NO
| NG | 5 | 4 | 1 | 48 | 68.3 | 9.03 | 50 | 100.4 | 55 | 65.2 | 62.9 | 218.9 | 204.9 | 204.9 | NO
1 | OK | 35 | 23 | 28 | 42 | 28.4 | 8.91 | 50 | 100.4 | 55 | 66 | 62 | 213.7 | 212 | 212 | YES
| NG | 35 | 22 | 34 | 41 | 89.8 | 7.14 | 50 | 100.4 | 55 | 73 | 61 | 212.7 | 202.8 | 202.8 | NO
| NG | 4 | 3 | 1 | 48 | 68.3 | 8.62 | 50 | 100.4 | 55 | 66.8 | 62.9 | 218.9 | 204.9 | 204.9 | NO
2 | ** OPTIMAL ** | 23 | 24 | 28 | 42 | 28.4 | 7.81 | 50 | 100.4 | 55 | 70.2 | 60.6 | 212.9 | 212.7 | 212.7 | YES
| NG | 3 | 7 | 1 | 48 | 68.3 | 6.17 | 50 | 100.4 | 55 | 76.2 | 62.9 | 218.9 | 204.9 | 204.9 | NO
3 | OK | 24 | 38 | 28 | 42 | 28.4 | 6.86 | 50 | 100.4 | 55 | 73.8 | 60.6 | 212.9 | 212.7 | 212.7 | YES
| NG | 7 | 1 | 1 | 48 | 68.3 | 6.17 | 50 | 100.4 | 55 | 76.2 | 62.9 | 218.9 | 204.9 | 204.9 | NO
| NG | 1 | 0 | 0 | 48 | 76.1 | 6.17 | 50 | 100.4 | 55 | 76.2 | 62.9 | 218.9 | 205 | 205 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 61-004204
TR_B (available) | 41-000900
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 100.4
TR_B Baseline Loading% | 55
Total Scenarios Evaluated | 11
Feasible Scenarios | 3
--- Optimal Solution ---
Switch Parent Node | 23
Switch Child Node | 24
Tie Node (TR_A side) | 28
Tie Node (TR_B side) | 42
Tie Line Distance (m) | 28.4
Load Transferred (kW) | 7.81
TR_A Loading After (%) | 70.2
TR_B Loading After (%) | 60.6
Minimum Voltage (V) | 212.7