## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 22 | 21 | 34 | 45 | 1.9 | 9.4 | 50 | 86.1 | 57.4 | 49.9 | 80 | 222.5 | 208.7 | 208.7 | NO
| NG | 21 | 18 | 34 | 45 | 1.9 | 9.16 | 50 | 86.1 | 57.4 | 50.8 | 79.4 | 222.3 | 209.3 | 209.3 | NO
| NG | 18 | 16 | 34 | 45 | 1.9 | 8.92 | 50 | 86.1 | 57.4 | 51.7 | 78.7 | 222.1 | 209.9 | 209.9 | NO
1 | OK | 16 | 7 | 7 | 0 | 104.8 | 1.87 | 50 | 86.1 | 57.4 | 78.9 | 62 | 216.3 | 215.1 | 215.1 | YES
2 | ** OPTIMAL ** | 16 | 11 | 34 | 45 | 1.9 | 4.36 | 50 | 86.1 | 57.4 | 69.3 | 67.6 | 217.4 | 218.4 | 217.4 | YES
| NG | 16 | 20 | 20 | 0 | 112.7 | 2.69 | 50 | 86.1 | 57.4 | 75.6 | 64.2 | 219.1 | 209.8 | 209.8 | NO
| NG | 6 | 5 | 4 | 40 | 90.7 | 5.66 | 50 | 86.1 | 57.4 | 58.7 | 71.9 | 220.2 | 204.1 | 204.1 | NO
| NG | 6 | 17 | 17 | 0 | 153.9 | 5.13 | 50 | 86.1 | 57.4 | 66.8 | 70.6 | 214.7 | 203.6 | 203.6 | NO
3 | OK | 11 | 12 | 34 | 45 | 1.9 | 3.29 | 50 | 86.1 | 57.4 | 73.5 | 65.1 | 216.3 | 218.4 | 216.3 | YES
4 | OK | 12 | 13 | 34 | 45 | 1.9 | 2.81 | 50 | 86.1 | 57.4 | 75.3 | 63.9 | 216.3 | 218.3 | 216.3 | YES
5 | OK | 13 | 8 | 34 | 45 | 1.9 | 1.98 | 50 | 86.1 | 57.4 | 78.5 | 59.4 | 216.2 | 218.2 | 216.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 61-004721
TR_B (available) | 54-004917
TR_A Rated kVA | 30
TR_B Rated kVA | 50
TR_A Baseline Loading% | 86.1
TR_B Baseline Loading% | 57.4
Total Scenarios Evaluated | 11
Feasible Scenarios | 5
--- Optimal Solution ---
Switch Parent Node | 16
Switch Child Node | 11
Tie Node (TR_A side) | 34
Tie Node (TR_B side) | 45
Tie Line Distance (m) | 1.9
Load Transferred (kW) | 4.36
TR_A Loading After (%) | 69.3
TR_B Loading After (%) | 67.6
Minimum Voltage (V) | 217.4