## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 32 | 11 | 21 | 3 | 32 | 2.93 | 50 | 88 | 30.6 | 76.7 | 41.9 | 216 | 223 | 216 | YES
2 | OK | 32 | 30 | 33 | 0 | 44.5 | 6.73 | 50 | 88 | 30.6 | 32.4 | 57.4 | 225.6 | 213 | 213 | YES
3 | ** OPTIMAL ** | 32 | 3 | 2 | 23 | 82.8 | 11.36 | 50 | 88 | 30.6 | 43.7 | 45.8 | 218.7 | 221.3 | 218.7 | YES
4 | OK | 11 | 12 | 21 | 3 | 32 | 2.85 | 50 | 88 | 30.6 | 77 | 41.6 | 216 | 223 | 216 | YES
5 | OK | 30 | 33 | 33 | 0 | 44.5 | 6.65 | 50 | 88 | 30.6 | 61.8 | 57.1 | 214.1 | 213 | 213 | YES
6 | OK | 3 | 20 | 20 | 23 | 117.5 | 6.11 | 50 | 88 | 30.6 | 59.1 | 38.5 | 217.6 | 223.8 | 217.6 | YES
7 | OK | 12 | 21 | 21 | 3 | 32 | 2.78 | 50 | 88 | 30.6 | 77.3 | 41.3 | 216 | 223.1 | 216 | YES
8 | OK | 33 | 18 | 18 | 0 | 88.1 | 6.63 | 50 | 88 | 30.6 | 61.9 | 56.9 | 214.1 | 213.8 | 213.8 | YES
9 | OK | 20 | 1 | 1 | 0 | 146.6 | 5.88 | 50 | 88 | 30.6 | 60 | 53.5 | 217.4 | 219.3 | 217.4 | YES
10 | OK | 18 | 19 | 19 | 0 | 157.8 | 5.39 | 50 | 88 | 30.6 | 66.6 | 51.9 | 214.1 | 216 | 214.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 61-005493
TR_B (available) | 46-000169
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 88
TR_B Baseline Loading% | 30.6
Total Scenarios Evaluated | 10
Feasible Scenarios | 10
--- Optimal Solution ---
Switch Parent Node | 32
Switch Child Node | 3
Tie Node (TR_A side) | 2
Tie Node (TR_B side) | 23
Tie Line Distance (m) | 82.8
Load Transferred (kW) | 11.36
TR_A Loading After (%) | 43.7
TR_B Loading After (%) | 45.8
Minimum Voltage (V) | 218.7