## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 36 | 41 | 53 | 32 | 1.4 | 2.95 | 50 | 83.6 | 70 | 72.3 | 81.4 | 210.9 | 218.2 | 210.9 | NO
| NG | 41 | 54 | 53 | 32 | 1.4 | 2.74 | 50 | 83.6 | 70 | 73.1 | 80.6 | 210.9 | 218.9 | 210.9 | NO
| NG | 54 | 26 | 53 | 32 | 1.4 | 2.61 | 50 | 83.6 | 70 | 73.6 | 80.1 | 210.9 | 219.2 | 210.9 | NO
1 | ** OPTIMAL ** | 26 | 25 | 53 | 32 | 1.4 | 2.21 | 50 | 83.6 | 70 | 75.1 | 78.6 | 210.6 | 219.2 | 210.6 | YES
| NG | 25 | 1 | 53 | 32 | 1.4 | 1.41 | 50 | 83.6 | 70 | 78.2 | 75.5 | 210 | 219.2 | 210 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 61-005545
TR_B (available) | 63-020204
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 83.6
TR_B Baseline Loading% | 70
Total Scenarios Evaluated | 5
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 26
Switch Child Node | 25
Tie Node (TR_A side) | 53
Tie Node (TR_B side) | 32
Tie Line Distance (m) | 1.4
Load Transferred (kW) | 2.21
TR_A Loading After (%) | 75.1
TR_B Loading After (%) | 78.6
Minimum Voltage (V) | 210.6