## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 16 | 13 | 31 | 30 | 37.4 | 5.78 | 50 | 83.6 | 25.7 | 60.5 | 49.8 | 215.4 | 204 | 204 | NO
| NG | 13 | 14 | 31 | 30 | 37.4 | 5.78 | 50 | 83.6 | 25.7 | 60.5 | 49.8 | 215.4 | 204 | 204 | NO
| NG | 14 | 33 | 31 | 30 | 37.4 | 5.78 | 50 | 83.6 | 25.7 | 60.5 | 49.8 | 215.4 | 204 | 204 | NO
| NG | 33 | 11 | 31 | 30 | 37.4 | 5.66 | 50 | 83.6 | 25.7 | 61 | 48.2 | 215.3 | 205.7 | 205.7 | NO
| NG | 11 | 12 | 31 | 30 | 37.4 | 5.43 | 50 | 83.6 | 25.7 | 61.9 | 48.2 | 215.3 | 205.7 | 205.7 | NO
| NG | 12 | 9 | 31 | 30 | 37.4 | 5.43 | 50 | 83.6 | 25.7 | 61.9 | 48.2 | 215.3 | 205.7 | 205.7 | NO
| NG | 9 | 52 | 31 | 30 | 37.4 | 5.43 | 50 | 83.6 | 25.7 | 61.9 | 44.3 | 215.3 | 209.5 | 209.5 | NO
1 | ** OPTIMAL ** | 52 | 22 | 31 | 30 | 37.4 | 4.55 | 50 | 83.6 | 25.7 | 65.3 | 40.1 | 215.4 | 213.6 | 213.6 | YES
2 | OK | 22 | 23 | 31 | 30 | 37.4 | 3.56 | 50 | 83.6 | 25.7 | 69.2 | 40.1 | 214.3 | 213.6 | 213.6 | YES
3 | OK | 23 | 40 | 31 | 30 | 37.4 | 2.46 | 50 | 83.6 | 25.7 | 73.5 | 35.5 | 213 | 217.7 | 213 | YES
4 | OK | 40 | 30 | 31 | 30 | 37.4 | 2.14 | 50 | 83.6 | 25.7 | 74.8 | 34.2 | 212.6 | 218.9 | 212.6 | YES
5 | OK | 30 | 31 | 31 | 30 | 37.4 | 1.88 | 50 | 83.6 | 25.7 | 75.9 | 33.1 | 212.3 | 219.7 | 212.3 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 61-005545
TR_B (available) | 66-000370
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 83.6
TR_B Baseline Loading% | 25.7
Total Scenarios Evaluated | 12
Feasible Scenarios | 5
--- Optimal Solution ---
Switch Parent Node | 52
Switch Child Node | 22
Tie Node (TR_A side) | 31
Tie Node (TR_B side) | 30
Tie Line Distance (m) | 37.4
Load Transferred (kW) | 4.55
TR_A Loading After (%) | 65.3
TR_B Loading After (%) | 40.1
Minimum Voltage (V) | 213.6