## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 42 | 37 | 56 | 103 | 3.6 | 30.18 | 50 | 81.9 | 49.5 | 46.4 | 74.8 | 216.5 | 179.4 | 179.4 | NO
| NG | 37 | 52 | 56 | 103 | 3.6 | 27.67 | 50 | 81.9 | 49.5 | 49.3 | 72.8 | 216.5 | 178.7 | 178.7 | NO
| NG | 52 | 25 | 56 | 103 | 3.6 | 25.09 | 50 | 81.9 | 49.5 | 52.2 | 70.9 | 215.8 | 176.4 | 176.4 | NO
| NG | 25 | 24 | 56 | 103 | 3.6 | 24.92 | 50 | 81.9 | 49.5 | 52.4 | 70.8 | 215.9 | 176.3 | 176.3 | NO
| NG | 24 | 54 | 56 | 103 | 3.6 | 20.57 | 50 | 81.9 | 49.5 | 57.5 | 66 | 215.9 | 194.1 | 194.1 | NO
| NG | 54 | 53 | 56 | 103 | 3.6 | 19.56 | 50 | 81.9 | 49.5 | 58.6 | 65.2 | 215.9 | 193.9 | 193.9 | NO
1 | OK | 53 | 67 | 56 | 103 | 3.6 | 12.84 | 50 | 81.9 | 49.5 | 66.6 | 59.3 | 215.9 | 212.1 | 212.1 | YES
2 | OK | 67 | 66 | 56 | 103 | 3.6 | 9.97 | 50 | 81.9 | 49.5 | 70 | 57.1 | 215.9 | 213.3 | 213.3 | YES
3 | OK | 66 | 1 | 56 | 103 | 3.6 | 9.74 | 50 | 81.9 | 49.5 | 70.3 | 56.9 | 215.9 | 213.1 | 213.1 | YES
4 | OK | 1 | 0 | 56 | 103 | 3.6 | 9.14 | 50 | 81.9 | 49.5 | 71 | 49.5 | 215.8 | 221.3 | 215.8 | YES
5 | OK | 0 | 55 | 72 | 123 | 104.2 | 9.14 | 50 | 81.9 | 49.5 | 71 | 56.5 | 215.8 | 210.6 | 210.6 | YES
6 | OK | 55 | 43 | 72 | 123 | 104.2 | 8.31 | 50 | 81.9 | 49.5 | 72 | 55.8 | 215.8 | 212.3 | 212.3 | YES
7 | OK | 43 | 44 | 72 | 123 | 104.2 | 7.65 | 50 | 81.9 | 49.5 | 72.8 | 55.3 | 215.8 | 212.9 | 212.9 | YES
8 | OK | 44 | 45 | 72 | 123 | 104.2 | 6.89 | 50 | 81.9 | 49.5 | 73.2 | 54.7 | 215.8 | 215 | 215 | YES
9 | OK | 45 | 9 | 72 | 123 | 104.2 | 6.89 | 50 | 81.9 | 49.5 | 73.6 | 54.7 | 215.8 | 215 | 215 | YES
10 | ** OPTIMAL ** | 9 | 8 | 8 | 103 | 122.6 | 5.2 | 50 | 81.9 | 49.5 | 74.7 | 53.4 | 215.8 | 219.1 | 215.8 | YES
11 | OK | 8 | 11 | 11 | 103 | 139.1 | 5.2 | 50 | 81.9 | 49.5 | 75.7 | 53.4 | 215.4 | 219.1 | 215.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 61-010136
TR_B (available) | 52-004070
TR_A Rated kVA | 100
TR_B Rated kVA | 160
TR_A Baseline Loading% | 81.9
TR_B Baseline Loading% | 49.5
Total Scenarios Evaluated | 17
Feasible Scenarios | 11
--- Optimal Solution ---
Switch Parent Node | 9
Switch Child Node | 8
Tie Node (TR_A side) | 8
Tie Node (TR_B side) | 103
Tie Line Distance (m) | 122.6
Load Transferred (kW) | 5.2
TR_A Loading After (%) | 74.7
TR_B Loading After (%) | 53.4
Minimum Voltage (V) | 215.8