## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 5 | 4 | 32 | 59 | 80.9 | 10.55 | 50 | 81.9 | 67.3 | 69.5 | 80.4 | 215.1 | 207.2 | 207.2 | NO
1 | OK | 4 | 16 | 32 | 59 | 80.9 | 4.61 | 50 | 81.9 | 67.3 | 76.4 | 72.8 | 214.5 | 214.2 | 214.2 | YES
2 | OK | 4 | 34 | 34 | 59 | 119 | 5.94 | 50 | 81.9 | 67.3 | 74.9 | 74.5 | 215 | 213.6 | 213.6 | YES
3 | OK | 16 | 31 | 32 | 59 | 80.9 | 2.32 | 50 | 81.9 | 67.3 | 79.2 | 70 | 214.5 | 217.6 | 214.5 | YES
4 | OK | 34 | 33 | 33 | 50 | 138.4 | 3.7 | 50 | 81.9 | 67.3 | 77.5 | 71.8 | 215 | 214.5 | 214.5 | YES
| NG | 58 | 65 | 30 | 65 | 1.8 | 12.65 | 50 | 81.9 | 67.3 | 66.7 | 83.3 | 215.5 | 204.5 | 204.5 | NO
| NG | 65 | 49 | 30 | 65 | 1.8 | 12.65 | 50 | 81.9 | 67.3 | 66.7 | 83.3 | 215.5 | 204.5 | 204.5 | NO
| NG | 49 | 50 | 30 | 65 | 1.8 | 11.6 | 50 | 81.9 | 67.3 | 67.9 | 82 | 215.5 | 204.3 | 204.3 | NO
| NG | 50 | 51 | 30 | 65 | 1.8 | 11.6 | 50 | 81.9 | 67.3 | 67.9 | 82 | 215.5 | 204.3 | 204.3 | NO
| NG | 51 | 46 | 30 | 65 | 1.8 | 6.8 | 50 | 81.9 | 67.3 | 73.7 | 75.8 | 215.5 | 207.4 | 207.4 | NO
| NG | 51 | 62 | 60 | 3 | 59.2 | 4.8 | 50 | 81.9 | 67.3 | 76.1 | 73.3 | 214.4 | 209.5 | 209.5 | NO
| NG | 46 | 47 | 30 | 65 | 1.8 | 6.8 | 50 | 81.9 | 67.3 | 73.7 | 75.8 | 215.5 | 207.4 | 207.4 | NO
5 | OK | 62 | 59 | 60 | 3 | 59.2 | 2.62 | 50 | 81.9 | 67.3 | 78.6 | 70.5 | 214.4 | 214.7 | 214.4 | YES
6 | OK | 47 | 21 | 30 | 65 | 1.8 | 4.83 | 50 | 81.9 | 67.3 | 76 | 73.3 | 215.1 | 211.2 | 211.2 | YES
7 | OK | 21 | 22 | 29 | 3 | 56.5 | 2.08 | 50 | 81.9 | 67.3 | 79.4 | 69.9 | 215 | 213.3 | 213.3 | YES
8 | ** OPTIMAL ** | 21 | 27 | 30 | 65 | 1.8 | 2.75 | 50 | 81.9 | 67.3 | 78.5 | 70.6 | 214.6 | 217 | 214.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 61-010136
TR_B (available) | 54-003173
TR_A Rated kVA | 100
TR_B Rated kVA | 100
TR_A Baseline Loading% | 81.9
TR_B Baseline Loading% | 67.3
Total Scenarios Evaluated | 16
Feasible Scenarios | 8
--- Optimal Solution ---
Switch Parent Node | 21
Switch Child Node | 27
Tie Node (TR_A side) | 30
Tie Node (TR_B side) | 65
Tie Line Distance (m) | 1.8
Load Transferred (kW) | 2.75
TR_A Loading After (%) | 78.5
TR_B Loading After (%) | 70.6
Minimum Voltage (V) | 214.6