## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 37 | 38 | 38 | 18 | 85 | 2.51 | 50 | 81.9 | 73.5 | 79 | 79.3 | 214.4 | 218.6 | 214.4 | YES
| NG | 35 | 36 | 36 | 18 | 29.4 | 3.2 | 50 | 81.9 | 73.5 | 78.1 | 81 | 215.3 | 216.9 | 215.3 | NO
2 | OK | 38 | 39 | 39 | 18 | 91.9 | 2.25 | 50 | 81.9 | 73.5 | 79.3 | 78.7 | 214.4 | 218.6 | 214.4 | YES
3 | OK | 39 | 13 | 13 | 27 | 112 | 2.04 | 50 | 81.9 | 73.5 | 79.5 | 78.2 | 214.4 | 218.6 | 214.4 | YES
4 | ** OPTIMAL ** | 12 | 69 | 69 | 27 | 159.3 | 2.62 | 50 | 81.9 | 73.5 | 78.7 | 79.7 | 215.4 | 215.8 | 215.4 | YES
5 | OK | 16 | 31 | 32 | 27 | 78.5 | 2.32 | 50 | 81.9 | 73.5 | 79.2 | 78.9 | 214.5 | 218.4 | 214.5 | YES
6 | OK | 33 | 3 | 3 | 27 | 127.1 | 2.07 | 50 | 81.9 | 73.5 | 79.4 | 78.4 | 215 | 217 | 215 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 61-010136
TR_B (available) | 66-004379
TR_A Rated kVA | 100
TR_B Rated kVA | 50
TR_A Baseline Loading% | 81.9
TR_B Baseline Loading% | 73.5
Total Scenarios Evaluated | 7
Feasible Scenarios | 6
--- Optimal Solution ---
Switch Parent Node | 12
Switch Child Node | 69
Tie Node (TR_A side) | 69
Tie Node (TR_B side) | 27
Tie Line Distance (m) | 159.3
Load Transferred (kW) | 2.62
TR_A Loading After (%) | 78.7
TR_B Loading After (%) | 79.7
Minimum Voltage (V) | 215.4