## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 65 | 72 | 70 | 16 | 2 | 3.47 | 50 | 79.5 | 22.7 | 71.4 |  | 215.5 | 5.0808e+58 | 215.5 | NO
| NG | 65 | 21 | 98 | 16 | 1.5 | 10.73 | 50 | 79.5 | 22.7 | [5 empty] | NO | TR_A sim: loading 7722% (degenerate)
| NG | 72 | 73 | 75 | 16 | 143.5 | 1.78 | 50 | 79.5 | 22.7 | 75.3 |  | 215.5 | 5.0808e+58 | 215.5 | NO
1 | OK | 72 | 83 | 70 | 16 | 2 | 1.3 | 50 | 79.5 | 22.7 | 76.5 | 22.7 | 215.6 | 225.2 | 215.6 | YES
| NG | 21 | 22 | 98 | 16 | 1.5 | 9.83 | 50 | 79.5 | 22.7 | 0 | 36.9 | 6 | 215.3 | 6 | NO
| NG | 73 | 74 | 75 | 16 | 143.5 | 1.3 | 50 | 79.5 | 22.7 | 76.4 |  | 215.5 | 5.0808e+58 | 215.5 | NO
| NG | 22 | 23 | 98 | 16 | 1.5 | 9.46 | 50 | 79.5 | 22.7 | 0 | 36.9 | 21.1 | 215.3 | 21.1 | NO
| NG | 23 | 24 | 3 | 16 | 145.6 | 4.33 | 50 | 79.5 | 22.7 | 0 | 30.1 | 5.2 | 221.5 | 5.2 | NO
2 | OK | 23 | 92 | 98 | 16 | 1.5 | 5.02 | 50 | 79.5 | 22.7 | 65 | 28.8 | 216.8 | 222.8 | 216.8 | YES
| NG | 24 | 50 | 3 | 16 | 145.6 | 3.86 | 50 | 79.5 | 22.7 | [5 empty] | NO | TR_A sim: loading 949% (degenerate)
3 | OK | 92 | 4 | 98 | 16 | 1.5 | 4.2 | 50 | 79.5 | 22.7 | 66.9 | 28.2 | 216.8 | 223.2 | 216.8 | YES
| NG | 50 | 49 | 3 | 16 | 145.6 | 3.4 | 50 | 79.5 | 22.7 | 0 | 30.1 | 7.9 | 221.5 | 7.9 | NO
4 | ** OPTIMAL ** | 4 | 5 | 98 | 16 | 1.5 | 3.6 | 50 | 79.5 | 22.7 | 68.2 | 25.9 | 216.8 | 224.6 | 216.8 | YES
| NG | 49 | 26 | 3 | 16 | 145.6 | 3.4 | 50 | 79.5 | 22.7 | 5.4 | 30.1 | 10.4 | 221.5 | 10.4 | NO
5 | OK | 5 | 6 | 98 | 16 | 1.5 | 1.3 | 50 | 79.5 | 22.7 | 73.5 | 25.9 | 215.7 | 224.6 | 215.7 | YES
| NG | 26 | 25 | 3 | 16 | 145.6 | 2.92 | 50 | 79.5 | 22.7 | 6 | 30.1 | 7.9 | 221.5 | 7.9 | NO
6 | OK | 6 | 7 | 98 | 16 | 1.5 | 0.89 | 50 | 79.5 | 22.7 | 74.5 | 24.3 | 215.7 | 224.9 | 215.7 | YES
| NG | 25 | 36 | 3 | 16 | 145.6 | 2.19 | 50 | 79.5 | 22.7 | 171.5 | 30.1 | 8.3 | 221.5 | 8.3 | NO
7 | OK | 7 | 8 | 98 | 16 | 1.5 | 0.25 | 50 | 79.5 | 22.7 | 75.9 | 23.3 | 215.5 | 225.1 | 215.5 | YES
| NG | 36 | 100 | 3 | 16 | 145.6 | 1.9 | 50 | 79.5 | 22.7 | 4 | 30.1 | 8.4 | 221.5 | 8.4 | NO
8 | OK | 8 | 9 | 98 | 16 | 1.5 | 0.25 | 50 | 79.5 | 22.7 | 75.9 | 23.3 | 215.5 | 225.1 | 215.5 | YES
| NG | 100 | 89 | 3 | 16 | 145.6 | 1.49 | 50 | 79.5 | 22.7 | 4 | 28.4 | 8.4 | 222.6 | 8.4 | NO
9 | OK | 9 | 10 | 98 | 16 | 1.5 | 0.25 | 50 | 79.5 | 22.7 | 78.9 | 23.3 | 215.5 | 225.1 | 215.5 | YES
| NG | 89 | 51 | 3 | 16 | 145.6 | 0.87 | 50 | 79.5 | 22.7 | 1.3 | 26 | 8.4 | 224.2 | 8.4 | NO
10 | OK | 10 | 11 | 98 | 16 | 1.5 | 0.08 | 50 | 79.5 | 22.7 | 79.3 | 22.7 | 215.5 | 225.2 | 215.5 | YES
| NG | 51 | 52 | 3 | 16 | 145.6 | 0.87 | 50 | 79.5 | 22.7 | 171.5 | 26 | 8.3 | 224.2 | 8.3 | NO
| NG | 52 | 16 | 3 | 16 | 145.6 | 0.51 | 50 | 79.5 | 22.7 | 1.3 | 24.6 | 16.8 | 224.9 | 16.8 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 62-001505
TR_B (available) | 54-006200
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 79.5
TR_B Baseline Loading% | 22.7
Total Scenarios Evaluated | 27
Feasible Scenarios | 10
--- Optimal Solution ---
Switch Parent Node | 4
Switch Child Node | 5
Tie Node (TR_A side) | 98
Tie Node (TR_B side) | 16
Tie Line Distance (m) | 1.5
Load Transferred (kW) | 3.6
TR_A Loading After (%) | 68.2
TR_B Loading After (%) | 25.9
Minimum Voltage (V) | 216.8