## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 8 | 23 | 16 | 10 | 35.9 | 5.23 | 50 | 21.7 | 4.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 23 | 18 | 16 | 10 | 35.9 | 5.23 | 50 | 21.7 | 4.2 | 15.7 | 6.6 | 228 | 228 | 228 | YES
2 | OK | 18 | 7 | 16 | 10 | 35.9 | 4.93 | 50 | 21.7 | 4.2 | 16 | 6.4 | 228 | 228 | 228 | YES
3 | OK | 7 | 6 | 16 | 10 | 35.9 | 4.41 | 50 | 21.7 | 4.2 | 16.6 | 6.2 | 228 | 228 | 228 | YES
4 | ** OPTIMAL ** | 6 | 5 | 16 | 10 | 35.9 | 4.2 | 50 | 21.7 | 4.2 | 16.9 | 6.1 | 228 | 228 | 228 | YES
5 | OK | 5 | 1 | 16 | 10 | 35.9 | 0.76 | 50 | 21.7 | 4.2 | 20.8 | 4.5 | 227.9 | 228 | 227.9 | YES
6 | OK | 1 | 21 | 16 | 10 | 35.9 | 0.76 | 50 | 21.7 | 4.2 | 20.8 | 4.5 | 227.9 | 228 | 227.9 | YES
7 | OK | 21 | 16 | 16 | 10 | 35.9 | 0.76 | 50 | 21.7 | 4.2 | 20.8 | 4.5 | 227.9 | 228 | 227.9 | YES
8 | OK | 16 | 17 | 17 | 14 | 40.4 | 0.76 | 50 | 21.7 | 4.2 | 20.8 | 4.5 | 227.9 | 228 | 227.9 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 62-001806
TR_B (available) | 37-018162
TR_A Rated kVA | 100
TR_B Rated kVA | 250
TR_A Baseline Loading% | 21.7
TR_B Baseline Loading% | 4.2
Total Scenarios Evaluated | 9
Feasible Scenarios | 8
--- Optimal Solution ---
Switch Parent Node | 6
Switch Child Node | 5
Tie Node (TR_A side) | 16
Tie Node (TR_B side) | 10
Tie Line Distance (m) | 35.9
Load Transferred (kW) | 4.2
TR_A Loading After (%) | 16.9
TR_B Loading After (%) | 6.1
Minimum Voltage (V) | 228