## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 8 | 9 | 2 | 13 | 43.6 | 13.66 | 50 | 21.7 | 25.3 | 6 | 35.2 | 229.8 | 222.8 | 222.8 | YES
2 | OK | 8 | 23 | 1 | 10 | 42.5 | 5.23 | 50 | 21.7 | 25.3 | 15.7 | 29.1 | 228 | 224 | 224 | YES
3 | OK | 9 | 2 | 2 | 13 | 43.6 | 8.67 | 50 | 21.7 | 25.3 | 11.7 | 31.6 | 229.1 | 223.4 | 223.4 | YES
4 | OK | 23 | 18 | 1 | 10 | 42.5 | 5.23 | 50 | 21.7 | 25.3 | 15.7 | 29.1 | 228 | 224 | 224 | YES
5 | OK | 2 | 3 | 3 | 13 | 77.1 | 1.18 | 50 | 21.7 | 25.3 | 20.3 | 26.2 | 228.3 | 224.3 | 224.3 | YES
6 | OK | 2 | 4 | 4 | 13 | 43.7 | 6.02 | 50 | 21.7 | 25.3 | 14.4 | 29.7 | 229.2 | 223.9 | 223.9 | YES
7 | OK | 18 | 7 | 1 | 10 | 42.5 | 4.93 | 50 | 21.7 | 25.3 | 16 | 28.9 | 228 | 224 | 224 | YES
8 | OK | 3 | 12 | 12 | 13 | 79.1 | 1.18 | 50 | 21.7 | 25.3 | 20.3 | 25.3 | 228.3 | 224.2 | 224.2 | YES
9 | OK | 4 | 20 | 20 | 13 | 44 | 6.02 | 50 | 21.7 | 25.3 | 14.7 | 29.7 | 229.1 | 223.9 | 223.9 | YES
10 | OK | 7 | 6 | 1 | 10 | 42.5 | 4.41 | 50 | 21.7 | 25.3 | 16.6 | 28.5 | 228 | 224 | 224 | YES
11 | OK | 20 | 10 | 10 | 13 | 44.3 | 6.02 | 50 | 21.7 | 25.3 | 14.7 | 29.7 | 229.1 | 223.9 | 223.9 | YES
12 | OK | 6 | 5 | 1 | 10 | 42.5 | 4.2 | 50 | 21.7 | 25.3 | 16.9 | 28.3 | 228 | 224 | 224 | YES
13 | OK | 10 | 11 | 11 | 13 | 60.3 | 6.02 | 50 | 21.7 | 25.3 | 14.7 | 29.7 | 229.1 | 223.9 | 223.9 | YES
14 | OK | 5 | 1 | 1 | 10 | 42.5 | 0.76 | 50 | 21.7 | 25.3 | 20.8 | 25.9 | 227.9 | 224.2 | 224.2 | YES
15 | OK | 11 | 13 | 13 | 13 | 62.4 | 4.26 | 50 | 21.7 | 25.3 | 16.8 | 28.3 | 228.6 | 224.1 | 224.1 | YES
16 | OK | 11 | 19 | 19 | 13 | 67 | 0.62 | 50 | 21.7 | 25.3 | 21 | 25.3 | 227.7 | 224.2 | 224.2 | YES
17 | OK | 1 | 21 | 21 | 32 | 47.4 | 0.76 | 50 | 21.7 | 25.3 | 20.8 | 25.9 | 227.9 | 224.2 | 224.2 | YES
18 | OK | 13 | 0 | 0 | 13 | 88.4 | 4.17 | 50 | 21.7 | 25.3 | 16.9 | 28.3 | 228.6 | 224.1 | 224.1 | YES
19 | OK | 21 | 16 | 16 | 32 | 48.6 | 0.76 | 50 | 21.7 | 25.3 | 20.8 | 25.9 | 227.9 | 224.2 | 224.2 | YES
20 | ** OPTIMAL ** | 0 | 14 | 14 | 13 | 96.1 | 2.07 | 50 | 21.7 | 25.3 | 19.3 | 26.8 | 228.2 | 224.3 | 224.3 | YES
21 | OK | 0 | 15 | 15 | 13 | 132.4 | 1.05 | 50 | 21.7 | 25.3 | 20.5 | 26.1 | 228.3 | 224.2 | 224.2 | YES
22 | OK | 16 | 17 | 17 | 32 | 105.2 | 0.76 | 50 | 21.7 | 25.3 | 20.8 | 25.9 | 227.9 | 224.2 | 224.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 62-001806
TR_B (available) | 65-034282
TR_A Rated kVA | 100
TR_B Rated kVA | 160
TR_A Baseline Loading% | 21.7
TR_B Baseline Loading% | 25.3
Total Scenarios Evaluated | 22
Feasible Scenarios | 22
--- Optimal Solution ---
Switch Parent Node | 0
Switch Child Node | 14
Tie Node (TR_A side) | 14
Tie Node (TR_B side) | 13
Tie Line Distance (m) | 96.1
Load Transferred (kW) | 2.07
TR_A Loading After (%) | 19.3
TR_B Loading After (%) | 26.8
Minimum Voltage (V) | 224.3