## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 29 | 33 | 47 | 10 | 127.5 | 13.82 | 50 | 88.3 | 23.1 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 33 | 41 | 47 | 10 | 127.5 | 13.82 | 50 | 88.3 | 23.1 | 55.2 | 84.1 | 220.4 | 183.5 | 183.5 | NO
| NG | 41 | 31 | 47 | 10 | 127.5 | 13.38 | 50 | 88.3 | 23.1 | 56.2 | 81.7 | 220.2 | 185.6 | 185.6 | NO
| NG | 31 | 30 | 47 | 10 | 127.5 | 10.95 | 50 | 88.3 | 23.1 | 61.8 | 69.4 | 219 | 196.1 | 196.1 | NO
| NG | 30 | 32 | 47 | 10 | 127.5 | 8.22 | 50 | 88.3 | 23.1 | 68.1 | 56.9 | 219 | 203.6 | 203.6 | NO
| NG | 32 | 38 | 47 | 10 | 127.5 | 7.53 | 50 | 88.3 | 23.1 | 69.7 | 53.9 | 219 | 205.4 | 205.4 | NO
1 | OK | 38 | 42 | 40 | 10 | 141.4 | 6.47 | 50 | 88.3 | 23.1 | 72.1 | 49.1 | 219 | 211.1 | 211.1 | YES
2 | OK | 42 | 40 | 40 | 10 | 141.4 | 6.45 | 50 | 88.3 | 23.1 | 72.2 | 49 | 219 | 211.1 | 211.1 | YES
3 | ** OPTIMAL ** | 40 | 39 | 39 | 10 | 149.3 | 5.14 | 50 | 88.3 | 23.1 | 75.3 | 43.5 | 219 | 214.6 | 214.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 62-002085
TR_B (available) | 56-013534
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 88.3
TR_B Baseline Loading% | 23.1
Total Scenarios Evaluated | 9
Feasible Scenarios | 3
--- Optimal Solution ---
Switch Parent Node | 40
Switch Child Node | 39
Tie Node (TR_A side) | 39
Tie Node (TR_B side) | 10
Tie Line Distance (m) | 149.3
Load Transferred (kW) | 5.14
TR_A Loading After (%) | 75.3
TR_B Loading After (%) | 43.5
Minimum Voltage (V) | 214.6