## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 0 | 25 | 32 | 23 | 67.8 | 20.91 | 50 | 79.5 | 54 | 30.7 | 64.4 | 218.6 | 212.4 | 212.4 | YES
2 | ** OPTIMAL ** | 25 | 26 | 32 | 23 | 67.8 | 17.83 | 50 | 79.5 | 54 | 37.7 | 64.4 | 218.6 | 212.4 | 212.4 | YES
3 | OK | 26 | 15 | 32 | 23 | 67.8 | 17.54 | 50 | 79.5 | 54 | 38.4 | 64 | 218.6 | 212.4 | 212.4 | YES
4 | OK | 15 | 16 | 32 | 23 | 67.8 | 11.46 | 50 | 79.5 | 54 | 52.6 | 64 | 215.5 | 212.4 | 212.4 | YES
5 | OK | 15 | 21 | 21 | 23 | 204.2 | 6.08 | 50 | 79.5 | 54 | 65.4 | 61.4 | 214.4 | 212.3 | 212.3 | YES
6 | OK | 16 | 24 | 32 | 23 | 67.8 | 9.06 | 50 | 79.5 | 54 | 58.1 | 63.9 | 215.5 | 212.4 | 212.4 | YES
7 | OK | 24 | 6 | 6 | 23 | 168.8 | 0.85 | 50 | 79.5 | 54 | 77.5 | 55 | 214.5 | 212.1 | 212.1 | YES
8 | OK | 24 | 19 | 32 | 23 | 67.8 | 8.21 | 50 | 79.5 | 54 | 60.1 | 63.9 | 215.5 | 212.4 | 212.4 | YES
9 | OK | 19 | 20 | 32 | 23 | 67.8 | 6.95 | 50 | 79.5 | 54 | 63 | 62.4 | 215.5 | 212.4 | 212.4 | YES
10 | OK | 20 | 34 | 32 | 23 | 67.8 | 4.52 | 50 | 79.5 | 54 | 68.6 | 59.4 | 215.5 | 212.3 | 212.3 | YES
11 | OK | 34 | 32 | 32 | 23 | 67.8 | 4.52 | 50 | 79.5 | 54 | 68.6 | 59.4 | 215.5 | 212.3 | 212.3 | YES
12 | OK | 32 | 10 | 10 | 10 | 116.5 | 4.52 | 50 | 79.5 | 54 | 68.6 | 59.4 | 215.5 | 212.4 | 212.4 | YES
13 | OK | 10 | 9 | 9 | 10 | 136.1 | 4.52 | 50 | 79.5 | 54 | 68.6 | 59.4 | 215.5 | 212.4 | 212.4 | YES
14 | OK | 9 | 7 | 7 | 10 | 159.8 | 3.15 | 50 | 79.5 | 54 | 71.8 | 57.7 | 215.5 | 212.3 | 212.3 | YES
| NG | 7 | 8 | 8 | 10 | 161.4 | 2.55 | 50 | 79.5 | 54 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 54.0% (degenerate)

## Summary
Parameter | Value
TR_A (overloaded) | 62-003074
TR_B (available) | 52-001935
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 79.5
TR_B Baseline Loading% | 54
Total Scenarios Evaluated | 15
Feasible Scenarios | 14
--- Optimal Solution ---
Switch Parent Node | 25
Switch Child Node | 26
Tie Node (TR_A side) | 32
Tie Node (TR_B side) | 23
Tie Line Distance (m) | 67.8
Load Transferred (kW) | 17.83
TR_A Loading After (%) | 37.7
TR_B Loading After (%) | 64.4
Minimum Voltage (V) | 212.4