## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 0 | 25 | 25 | 30 | 128.8 | 20.91 | 50 | 79.5 | 22.1 | 30.7 | 29.5 | 218.6 | 210.5 | 210.5 | YES
2 | OK | 0 | 13 | 17 | 9 | 2.3 | 13.17 | 50 | 79.5 | 22.1 | 48.8 | 24.1 | 217.1 | 211.4 | 211.4 | YES
3 | OK | 25 | 26 | 26 | 30 | 166 | 17.83 | 50 | 79.5 | 22.1 | 37.7 | 25.8 | 218.6 | 211.2 | 211.2 | YES
4 | ** OPTIMAL ** | 13 | 14 | 14 | 9 | 80.6 | 4.89 | 50 | 79.5 | 22.1 | 68.2 | 22.1 | 215.3 | 212 | 212 | YES
5 | OK | 13 | 23 | 17 | 9 | 2.3 | 8.28 | 50 | 79.5 | 22.1 | 60.1 | 24.1 | 214.6 | 211.4 | 211.4 | YES
6 | OK | 14 | 27 | 27 | 9 | 145 | 0.98 | 50 | 79.5 | 22.1 | 77.2 | 22.1 | 215.1 | 212 | 212 | YES
7 | OK | 23 | 22 | 17 | 9 | 2.3 | 7.82 | 50 | 79.5 | 22.1 | 61.1 | 23.6 | 214.6 | 211.5 | 211.5 | YES
8 | OK | 22 | 18 | 17 | 9 | 2.3 | 1.28 | 50 | 79.5 | 22.1 | 76.6 | 23.6 | 214.6 | 211.5 | 211.5 | YES
| NG | 22 | 33 | 38 | 33 | 68.9 | 6.54 | 50 | 79.5 | 22.1 | 64.1 | 31.5 | 214.6 | 193.7 | 193.7 | NO
9 | OK | 18 | 17 | 17 | 9 | 2.3 | 0.75 | 50 | 79.5 | 22.1 | 77.8 | 23 | 214.6 | 211.7 | 211.7 | YES
| NG | 33 | 37 | 38 | 33 | 68.9 | 4.24 | 50 | 79.5 | 22.1 | 69.4 | 28 | 214.6 | 199.8 | 199.8 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 62-003074
TR_B (available) | 67-018334
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 79.5
TR_B Baseline Loading% | 22.1
Total Scenarios Evaluated | 11
Feasible Scenarios | 9
--- Optimal Solution ---
Switch Parent Node | 13
Switch Child Node | 14
Tie Node (TR_A side) | 14
Tie Node (TR_B side) | 9
Tie Line Distance (m) | 80.6
Load Transferred (kW) | 4.89
TR_A Loading After (%) | 68.2
TR_B Loading After (%) | 22.1
Minimum Voltage (V) | 212