## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 13 | 14 | 27 | 10 | 119 | 4.89 | 50 | 79.5 | 68.2 | 68.2 | 80.3 | 215.3 | 206.8 | 206.8 | NO
1 | OK | 14 | 27 | 27 | 10 | 119 | 0.98 | 50 | 79.5 | 68.2 | 77.2 | 70.6 | 215.1 | 211.3 | 211.3 | YES
2 | ** OPTIMAL ** | 22 | 18 | 17 | 28 | 51.2 | 1.28 | 50 | 79.5 | 68.2 | 76.6 | 71.1 | 214.6 | 212.4 | 212.4 | YES
3 | OK | 18 | 17 | 17 | 28 | 51.2 | 0.75 | 50 | 79.5 | 68.2 | 77.8 | 69.9 | 214.6 | 212.4 | 212.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 62-003074
TR_B (available) | 67-037581
TR_A Rated kVA | 50
TR_B Rated kVA | 50
TR_A Baseline Loading% | 79.5
TR_B Baseline Loading% | 68.2
Total Scenarios Evaluated | 4
Feasible Scenarios | 3
--- Optimal Solution ---
Switch Parent Node | 22
Switch Child Node | 18
Tie Node (TR_A side) | 17
Tie Node (TR_B side) | 28
Tie Line Distance (m) | 51.2
Load Transferred (kW) | 1.28
TR_A Loading After (%) | 76.6
TR_B Loading After (%) | 71.1
Minimum Voltage (V) | 212.4