## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 52 | 17 | 8 | 1 | 2.3 | 28.49 | 50 | 98.6 | 23.5 | 31.5 | 38.3 | 213.6 | 188.3 | 188.3 | NO
| NG | 17 | 2 | 8 | 1 | 2.3 | 25.81 | 50 | 98.6 | 23.5 | 37.6 | 36.6 | 213.4 | 194.8 | 194.8 | NO
1 | OK | 2 | 9 | 8 | 1 | 2.3 | 14.08 | 50 | 98.6 | 23.5 | 65.3 | 30.2 | 213.4 | 217.9 | 213.4 | YES
2 | ** OPTIMAL ** | 9 | 25 | 8 | 1 | 2.3 | 12.3 | 50 | 98.6 | 23.5 | 67.4 | 29.3 | 213.4 | 219 | 213.4 | YES
3 | OK | 25 | 4 | 8 | 1 | 2.3 | 12.01 | 50 | 98.6 | 23.5 | 70.1 | 29.2 | 212.9 | 219 | 212.9 | YES
4 | OK | 4 | 5 | 8 | 1 | 2.3 | 10.76 | 50 | 98.6 | 23.5 | 73.1 | 28.6 | 212.9 | 219.1 | 212.9 | YES
5 | OK | 5 | 37 | 8 | 1 | 2.3 | 9.55 | 50 | 98.6 | 23.5 | 75.9 | 28 | 212.9 | 222.1 | 212.9 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 62-003403
TR_B (available) | 60-023655
TR_A Rated kVA | 50
TR_B Rated kVA | 250
TR_A Baseline Loading% | 98.6
TR_B Baseline Loading% | 23.5
Total Scenarios Evaluated | 7
Feasible Scenarios | 5
--- Optimal Solution ---
Switch Parent Node | 9
Switch Child Node | 25
Tie Node (TR_A side) | 8
Tie Node (TR_B side) | 1
Tie Line Distance (m) | 2.3
Load Transferred (kW) | 12.3
TR_A Loading After (%) | 67.4
TR_B Loading After (%) | 29.3
Minimum Voltage (V) | 213.4