## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 52 | 12 | 42 | 37 | 14.5 | 13.28 | 50 | 98.6 | 33.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 52 | 17 | 8 | 7 | 25.2 | 28.49 | 50 | 98.6 | 33.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 12 | 13 | 42 | 37 | 14.5 | 13.28 | 50 | 98.6 | 33.7 | [5 empty] | NO | TR_B sim: not converged
| NG | 17 | 2 | 8 | 7 | 25.2 | 25.81 | 50 | 98.6 | 33.7 | 37.6 | 58.3 | 213.4 | 155.2 | 155.2 | NO
| NG | 13 | 14 | 42 | 37 | 14.5 | 11.42 | 50 | 98.6 | 33.7 | 71.3 | 44.8 | 213.3 | 155.8 | 155.8 | NO
| NG | 2 | 9 | 8 | 7 | 25.2 | 14.08 | 50 | 98.6 | 33.7 | 65.3 | 45.1 | 213.4 | 203.5 | 203.5 | NO
| NG | 14 | 15 | 42 | 37 | 14.5 | 9.59 | 50 | 98.6 | 33.7 | 75.5 | 43.8 | 212.4 | 162 | 162 | NO
| NG | 9 | 25 | 8 | 7 | 25.2 | 12.3 | 50 | 98.6 | 33.7 | 67.4 | 43.6 | 213.4 | 205.8 | 205.8 | NO
| NG | 15 | 16 | 42 | 37 | 14.5 | 9.59 | 50 | 98.6 | 33.7 | 75.5 | 43.8 | 212.4 | 162 | 162 | NO
| NG | 25 | 4 | 8 | 7 | 25.2 | 12.01 | 50 | 98.6 | 33.7 | 70.1 | 43.3 | 212.9 | 205.7 | 205.7 | NO
| NG | 16 | 47 | 42 | 37 | 14.5 | 9.59 | 50 | 98.6 | 33.7 | 75.5 | 43.8 | 212.4 | 162 | 162 | NO
| NG | 4 | 5 | 8 | 7 | 25.2 | 10.76 | 50 | 98.6 | 33.7 | 73.1 | 42.3 | 212.9 | 205.8 | 205.8 | NO
1 | ** OPTIMAL ** | 5 | 37 | 8 | 7 | 25.2 | 9.55 | 50 | 98.6 | 33.7 | 75.9 | 41.3 | 212.9 | 210.7 | 210.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 62-003403
TR_B (available) | 67-009528
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 98.6
TR_B Baseline Loading% | 33.7
Total Scenarios Evaluated | 13
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 5
Switch Child Node | 37
Tie Node (TR_A side) | 8
Tie Node (TR_B side) | 7
Tie Line Distance (m) | 25.2
Load Transferred (kW) | 9.55
TR_A Loading After (%) | 75.9
TR_B Loading After (%) | 41.3
Minimum Voltage (V) | 210.7