## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 12 | 13 | 24 | 0 | 19.9 | 27.04 | 50 | 73.4 | 17.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 12 | 7 | 8 | 1 | 49.3 | 4.26 | 50 | 73.4 | 17.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 13 | 29 | 24 | 0 | 19.9 | 27.04 | 50 | 73.4 | 17.5 | 9.8 | 73.3 | 227.2 | 189.5 | 189.5 | NO
1 | OK | 7 | 8 | 8 | 1 | 49.3 | 4.26 | 50 | 73.4 | 17.5 | 63.6 | 27.5 | 213.9 | 222 | 213.9 | YES
| NG | 29 | 26 | 24 | 0 | 19.9 | 26.7 | 50 | 73.4 | 17.5 | 10.6 | 72.2 | 227.2 | 191.5 | 191.5 | NO
2 | OK | 8 | 28 | 28 | 1 | 50.5 | 4.26 | 50 | 73.4 | 17.5 | 63.6 | 27.5 | 213.9 | 222 | 213.9 | YES
| NG | 26 | 27 | 24 | 0 | 19.9 | 25.98 | 50 | 73.4 | 17.5 | 12.2 | 70.6 | 227.1 | 194.3 | 194.3 | NO
3 | OK | 26 | 30 | 30 | 0 | 114 | 0.19 | 50 | 73.4 | 17.5 | 73 | 17.9 | 213.8 | 223.7 | 213.8 | YES
4 | OK | 28 | 2 | 2 | 1 | 56.1 | 4.26 | 50 | 73.4 | 17.5 | 63.6 | 27.4 | 213.9 | 222.4 | 213.9 | YES
| NG | 27 | 44 | 24 | 0 | 19.9 | 24.17 | 50 | 73.4 | 17.5 | 16.4 | 69.8 | 226.4 | 195.5 | 195.5 | NO
5 | OK | 30 | 31 | 31 | 0 | 120.4 | 0.06 | 50 | 73.4 | 17.5 | 73.3 | 17.6 | 213.9 | 223.7 | 213.9 | YES
6 | OK | 2 | 0 | 0 | 1 | 63.3 | 4.12 | 50 | 73.4 | 17.5 | 63.9 | 27.1 | 213.9 | 222.6 | 213.9 | YES
7 | OK | 44 | 32 | 24 | 0 | 19.9 | 12.11 | 50 | 73.4 | 17.5 | 26.9 | 38.2 | 226.3 | 221 | 221 | YES
8 | OK | 0 | 1 | 1 | 1 | 101.1 | 3.44 | 50 | 73.4 | 17.5 | 65.5 | 25.5 | 213.9 | 223.6 | 213.9 | YES
9 | OK | 32 | 33 | 24 | 0 | 19.9 | 11.07 | 50 | 73.4 | 17.5 | 46.8 | 37.8 | 223.2 | 221.7 | 221.7 | YES
10 | OK | 1 | 9 | 9 | 1 | 135.8 | 3.19 | 50 | 73.4 | 17.5 | 66.1 | 24.9 | 213.9 | 223.7 | 213.9 | YES
11 | OK | 33 | 41 | 24 | 0 | 19.9 | 11.07 | 50 | 73.4 | 17.5 | 46.8 | 37.8 | 223.2 | 221.7 | 221.7 | YES
12 | OK | 41 | 39 | 24 | 0 | 19.9 | 11.07 | 50 | 73.4 | 17.5 | 46.8 | 37.8 | 223.2 | 221.7 | 221.7 | YES
13 | OK | 39 | 35 | 24 | 0 | 19.9 | 9.05 | 50 | 73.4 | 17.5 | 51.4 | 37 | 223.1 | 221.6 | 221.6 | YES
14 | OK | 35 | 34 | 24 | 0 | 19.9 | 8.39 | 50 | 73.4 | 17.5 | 53 | 37 | 223.2 | 221.6 | 221.6 | YES
15 | OK | 34 | 6 | 24 | 0 | 19.9 | 8.39 | 50 | 73.4 | 17.5 | 53 | 37 | 223.2 | 221.6 | 221.6 | YES
16 | OK | 6 | 3 | 24 | 0 | 19.9 | 8.39 | 50 | 73.4 | 17.5 | 53 | 37 | 223.2 | 221.6 | 221.6 | YES
17 | OK | 3 | 4 | 24 | 0 | 19.9 | 8.39 | 50 | 73.4 | 17.5 | 53 | 37 | 223.2 | 221.6 | 221.6 | YES
18 | OK | 4 | 5 | 24 | 0 | 19.9 | 8.39 | 50 | 73.4 | 17.5 | 53 | 37 | 223.2 | 221.6 | 221.6 | YES
19 | OK | 5 | 16 | 24 | 0 | 19.9 | 7.85 | 50 | 73.4 | 17.5 | 54.3 | 35.7 | 222.2 | 221.3 | 221.3 | YES
20 | ** OPTIMAL ** | 16 | 18 | 24 | 0 | 19.9 | 6.33 | 50 | 73.4 | 17.5 | 57.8 | 32 | 222.4 | 222.3 | 222.3 | YES
| NG | 18 | 19 | 24 | 0 | 19.9 | 6.14 | 50 | 73.4 | 17.5 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 17.5% (degenerate)
21 | OK | 19 | 20 | 24 | 0 | 19.9 | 5.47 | 50 | 73.4 | 17.5 | 59.9 | 30.2 | 220.4 | 222.7 | 220.4 | YES
22 | OK | 20 | 21 | 24 | 0 | 19.9 | 5.18 | 50 | 73.4 | 17.5 | 60.6 | 29.5 | 220.4 | 222.7 | 220.4 | YES
23 | OK | 21 | 25 | 24 | 0 | 19.9 | 3 | 50 | 73.4 | 17.5 | 65.9 | 24.4 | 216.7 | 222.8 | 216.7 | YES
24 | OK | 25 | 22 | 24 | 0 | 19.9 | 2.37 | 50 | 73.4 | 17.5 | 67.5 | 22.9 | 214.7 | 222.8 | 214.7 | YES
25 | OK | 22 | 23 | 24 | 0 | 19.9 | 1.63 | 50 | 73.4 | 17.5 | 69.3 | 21.2 | 215.2 | 223.2 | 215.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 62-003544
TR_B (available) | 29-009936
TR_A Rated kVA | 50
TR_B Rated kVA | 50
TR_A Baseline Loading% | 73.4
TR_B Baseline Loading% | 17.5
Total Scenarios Evaluated | 32
Feasible Scenarios | 25
--- Optimal Solution ---
Switch Parent Node | 16
Switch Child Node | 18
Tie Node (TR_A side) | 24
Tie Node (TR_B side) | 0
Tie Line Distance (m) | 19.9
Load Transferred (kW) | 6.33
TR_A Loading After (%) | 57.8
TR_B Loading After (%) | 32
Minimum Voltage (V) | 222.3