## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 12 | 13 | 6 | 12 | 2.8 | 27.04 | 50 | 73.4 | 40.9 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 13 | 29 | 6 | 12 | 2.8 | 27.04 | 50 | 73.4 | 40.9 | 9.8 | 75.3 | 227.2 | 197.7 | 197.7 | NO
| NG | 29 | 26 | 6 | 12 | 2.8 | 26.7 | 50 | 73.4 | 40.9 | 10.6 | 74.8 | 227.2 | 199 | 199 | NO
| NG | 26 | 27 | 6 | 12 | 2.8 | 25.98 | 50 | 73.4 | 40.9 | 12.2 | 73.8 | 227.1 | 200.9 | 200.9 | NO
| NG | 27 | 44 | 6 | 12 | 2.8 | 24.17 | 50 | 73.4 | 40.9 | 16.4 | 71.6 | 226.4 | 200.7 | 200.7 | NO
1 | OK | 44 | 32 | 6 | 12 | 2.8 | 12.11 | 50 | 73.4 | 40.9 | 26.9 | 55.5 | 226.3 | 214.5 | 214.5 | YES
2 | OK | 32 | 33 | 6 | 12 | 2.8 | 11.07 | 50 | 73.4 | 40.9 | 46.8 | 54.3 | 223.2 | 214.3 | 214.3 | YES
3 | OK | 33 | 41 | 6 | 12 | 2.8 | 11.07 | 50 | 73.4 | 40.9 | 46.8 | 54.3 | 223.2 | 214.3 | 214.3 | YES
4 | OK | 41 | 39 | 6 | 12 | 2.8 | 11.07 | 50 | 73.4 | 40.9 | 46.8 | 52.3 | 223.2 | 214.1 | 214.1 | YES
5 | OK | 39 | 35 | 6 | 12 | 2.8 | 9.05 | 50 | 73.4 | 40.9 | 51.4 | 51.8 | 223.1 | 213.9 | 213.9 | YES
6 | OK | 35 | 34 | 6 | 12 | 2.8 | 8.39 | 50 | 73.4 | 40.9 | 53 | 51.1 | 223.2 | 213.8 | 213.8 | YES
7 | OK | 35 | 36 | 36 | 12 | 109.8 | 0.66 | 50 | 73.4 | 40.9 | 71.9 | 41.6 | 213.7 | 222.9 | 213.7 | YES
8 | OK | 34 | 6 | 6 | 12 | 2.8 | 8.39 | 50 | 73.4 | 40.9 | 53 | 51.1 | 223.2 | 213.8 | 213.8 | YES
9 | OK | 36 | 40 | 40 | 12 | 113.7 | 0.15 | 50 | 73.4 | 40.9 | 73.1 | 41 | 213.8 | 223 | 213.8 | YES
10 | OK | 6 | 3 | 3 | 12 | 9.6 | 8.39 | 50 | 73.4 | 40.9 | 53 | 51.1 | 223.2 | 213.9 | 213.9 | YES
11 | OK | 40 | 37 | 37 | 12 | 130.6 | 0.11 | 50 | 73.4 | 40.9 | 73.2 | 41 | 213.8 | 223 | 213.8 | YES
12 | OK | 3 | 4 | 4 | 12 | 42.8 | 8.39 | 50 | 73.4 | 40.9 | 53 | 51.1 | 223.2 | 213.9 | 213.9 | YES
13 | OK | 4 | 5 | 17 | 12 | 48.3 | 8.39 | 50 | 73.4 | 40.9 | 53 | 51 | 223.2 | 213.6 | 213.6 | YES
14 | OK | 5 | 16 | 16 | 12 | 62.1 | 7.85 | 50 | 73.4 | 40.9 | 54.3 | 50.4 | 222.2 | 213.8 | 213.8 | YES
15 | OK | 5 | 17 | 17 | 12 | 48.3 | 0.54 | 50 | 73.4 | 40.9 | 72.1 | 41.5 | 213.8 | 223 | 213.8 | YES
16 | ** OPTIMAL ** | 16 | 18 | 18 | 12 | 92.1 | 6.33 | 50 | 73.4 | 40.9 | 57.8 | 48.5 | 222.4 | 217.6 | 217.6 | YES
| NG | 18 | 19 | 19 | 12 | 94 | 6.14 | 50 | 73.4 | 40.9 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 40.9% (degenerate)
17 | OK | 19 | 20 | 20 | 12 | 132.3 | 5.47 | 50 | 73.4 | 40.9 | 59.9 | 47.5 | 220.4 | 217.4 | 217.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 62-003544
TR_B (available) | 46-002147
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 73.4
TR_B Baseline Loading% | 40.9
Total Scenarios Evaluated | 23
Feasible Scenarios | 17
--- Optimal Solution ---
Switch Parent Node | 16
Switch Child Node | 18
Tie Node (TR_A side) | 18
Tie Node (TR_B side) | 12
Tie Line Distance (m) | 92.1
Load Transferred (kW) | 6.33
TR_A Loading After (%) | 57.8
TR_B Loading After (%) | 48.5
Minimum Voltage (V) | 217.6