## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 18 | 22 | 56 | 37 | 62.5 | 15.38 | 50 | 82.9 | 12.1 | 20 | 12.1 | 226.7 | 218.6 | 218.6 | YES
2 | OK | 18 | 36 | 6 | 72 | 249.6 | 1.39 | 50 | 82.9 | 12.1 | 14.7 | 13.1 | 226.9 | 218.4 | 218.4 | YES
| NG | 22 | 11 | 56 | 37 | 62.5 | 12.14 | 50 | 82.9 | 12.1 | [5 empty] | NO | TR_A sim: loading inf% (degenerate)
| NG | 22 | 23 | 25 | 21 | 145.3 | 2.39 | 50 | 82.9 | 12.1 | 73.2 |  | 198.5 | 3687488.3 | 198.5 | NO
3 | OK | 36 | 37 | 6 | 72 | 249.6 | 1.09 | 50 | 82.9 | 12.1 | 15.9 | 12.9 | 226.9 | 218.5 | 218.5 | YES
| NG | 11 | 10 | 56 | 37 | 62.5 | 12.14 | 50 | 82.9 | 12.1 | [5 empty] | NO | TR_A sim: not converged
| NG | 23 | 25 | 25 | 21 | 145.3 | 1.56 | 50 | 82.9 | 12.1 | [5 empty] | NO | TR_B sim: not converged
4 | OK | 37 | 55 | 6 | 72 | 249.6 | 0.94 | 50 | 82.9 | 12.1 | 16.4 | 12.8 | 226.8 | 218.5 | 218.5 | YES
| NG | 10 | 9 | 56 | 37 | 62.5 | 12.14 | 50 | 82.9 | 12.1 | [5 empty] | NO | TR_A sim: loading inf% (degenerate)
5 | OK | 55 | 5 | 6 | 72 | 249.6 | 0.94 | 50 | 82.9 | 12.1 | 16.4 | 12.8 | 226.8 | 218.5 | 218.5 | YES
| NG | 9 | 8 | 56 | 37 | 62.5 | 10.34 | 50 | 82.9 | 12.1 |  | 12.1 | 34763905431.1 | 218.6 | 218.6 | NO
6 | OK | 5 | 6 | 6 | 72 | 249.6 | 0.89 | 50 | 82.9 | 12.1 | 16.6 | 12.7 | 226.8 | 218.5 | 218.5 | YES
7 | ** OPTIMAL ** | 8 | 20 | 56 | 37 | 62.5 | 10.34 | 50 | 82.9 | 12.1 | 0 | 12.1 | 5.0808e+58 | 218.6 | 218.6 | YES
| NG | 20 | 21 | 56 | 37 | 62.5 | 9.88 | 50 | 82.9 | 12.1 | [5 empty] | NO | TR_A sim: not converged
| NG | 21 | 40 | 56 | 37 | 62.5 | 8.81 | 50 | 82.9 | 12.1 | [5 empty] | NO | TR_A sim: loading inf% (degenerate)
| NG | 40 | 15 | 56 | 37 | 62.5 | 8.25 | 50 | 82.9 | 12.1 | [5 empty] | NO | TR_A sim: loading inf% (degenerate)
| NG | 15 | 16 | 56 | 37 | 62.5 | 8.25 | 50 | 82.9 | 12.1 | [5 empty] | NO | TR_A sim: not converged
| NG | 16 | 19 | 56 | 37 | 62.5 | 3.83 | 50 | 82.9 | 12.1 | [5 empty] | NO | TR_A sim: not converged
8 | OK | 19 | 43 | 56 | 37 | 62.5 | 3.83 | 50 | 82.9 | 12.1 | 65.8 | 12.1 | 212.7 | 218.6 | 212.7 | YES
9 | OK | 43 | 44 | 56 | 37 | 62.5 | 3.43 | 50 | 82.9 | 12.1 | 67.5 | 12.1 | 211.6 | 218.6 | 211.6 | YES
| NG | 44 | 45 | 56 | 37 | 62.5 | 2.76 | 50 | 82.9 | 12.1 | 70.4 | 12.1 | 209.3 | 218.6 | 209.3 | NO
| NG | 45 | 50 | 56 | 37 | 62.5 | 2.29 | 50 | 82.9 | 12.1 | 72.4 | 12.1 | 207.5 | 218.6 | 207.5 | NO
| NG | 50 | 51 | 56 | 37 | 62.5 | 1.92 | 50 | 82.9 | 12.1 | 74.1 | 12.1 | 206.1 | 218.6 | 206.1 | NO
| NG | 51 | 52 | 56 | 37 | 62.5 | 0.97 | 50 | 82.9 | 12.1 | 78.3 | 12.1 | 201.9 | 218.6 | 201.9 | NO
| NG | 52 | 53 | 56 | 37 | 62.5 | 0.97 | 50 | 82.9 | 12.1 | 78.3 | 12.1 | 201.9 | 218.6 | 201.9 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 62-004053
TR_B (available) | 29-011180
TR_A Rated kVA | 30
TR_B Rated kVA | 160
TR_A Baseline Loading% | 82.9
TR_B Baseline Loading% | 12.1
Total Scenarios Evaluated | 25
Feasible Scenarios | 9
--- Optimal Solution ---
Switch Parent Node | 8
Switch Child Node | 20
Tie Node (TR_A side) | 56
Tie Node (TR_B side) | 37
Tie Line Distance (m) | 62.5
Load Transferred (kW) | 10.34
TR_A Loading After (%) | 0
TR_B Loading After (%) | 12.1
Minimum Voltage (V) | 218.6