## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 18 | 17 | 3 | 5 | 64.1 | 3.84 | 50 | 82.9 | 61.4 | 68.1 | 76.6 | 198.8 | 213.8 | 198.8 | NO
1 | ** OPTIMAL ** | 18 | 36 | 36 | 5 | 207 | 1.39 | 50 | 82.9 | 61.4 | 14.7 | 66.9 | 226.9 | 218.7 | 218.7 | YES
| NG | 17 | 3 | 3 | 5 | 64.1 | 2.6 | 50 | 82.9 | 61.4 | 72.9 | 71.7 | 197.8 | 213.4 | 197.8 | NO
| NG | 22 | 23 | 24 | 23 | 191.5 | 2.39 | 50 | 82.9 | 61.4 | 73.2 |  | 198.5 | 2281055454697502 | 198.5 | NO
| NG | 3 | 2 | 2 | 5 | 98.3 | 2.47 | 50 | 82.9 | 61.4 | 73.4 | 71.2 | 197.6 | 213.3 | 197.6 | NO
| NG | 2 | 4 | 4 | 5 | 167.3 | 1.78 | 50 | 82.9 | 61.4 | 76 | 68.4 | 197.6 | 215.7 | 197.6 | NO
| NG | 16 | 19 | 49 | 22 | 282 | 3.83 | 50 | 82.9 | 61.4 | [5 empty] | NO | TR_A sim: not converged
2 | OK | 19 | 43 | 49 | 22 | 282 | 3.83 | 50 | 82.9 | 61.4 | 65.8 | 77 | 212.7 | 211.5 | 211.5 | YES
3 | OK | 43 | 44 | 49 | 22 | 282 | 3.43 | 50 | 82.9 | 61.4 | 67.5 | 75.3 | 211.6 | 213.1 | 211.6 | YES
| NG | 44 | 45 | 49 | 22 | 282 | 2.76 | 50 | 82.9 | 61.4 | 70.4 | 72.5 | 209.3 | 215.7 | 209.3 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 62-004053
TR_B (available) | 53-000095
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 82.9
TR_B Baseline Loading% | 61.4
Total Scenarios Evaluated | 10
Feasible Scenarios | 3
--- Optimal Solution ---
Switch Parent Node | 18
Switch Child Node | 36
Tie Node (TR_A side) | 36
Tie Node (TR_B side) | 5
Tie Line Distance (m) | 207
Load Transferred (kW) | 1.39
TR_A Loading After (%) | 14.7
TR_B Loading After (%) | 66.9
Minimum Voltage (V) | 218.7